## CBC Temporal
Id_Req | Desc_Req | ID_Req_BBDD | Descr_Req_BBDD | %Coincidencia | Resp_BBDD | Coment_BBDD | Nueva_Respuesta | Nuevos_comentarios
EFB-RS-117 | The levels are stated in dBA for the saloon HVAC noise measurements, with the following references: · Sound Pressure Levels: reference value is 20E-6 Pa (20 µPa) · Sound Power Levels: reference value is 1E-12 W (1 pW) · Velocity Levels: reference value is 1E-9 m/s (1 nm/s) · Aceleration Levels: reference value is 1E-6 m/s² · Mobility Levels: reference value is 1 m/Ns | EFB-RS-117 | The levels are stated in dBA for the saloon HVAC noise measurements, with the following references: · Sound Pressure Levels: reference value is 20E-6 Pa (20 µPa) · Sound Power Levels: reference value is 1E-12 W (1 pW) · Velocity Levels: reference value is 1E-9 m/s (1 nm/s) · Aceleration Levels: reference value is 1E-6 m/s² · Mobility Levels: reference value is 1 m/Ns | 100 | C |  | C
EFB-RS-118 | Measurements to proof the compliance with the limits set hereafter shall be carried out. Test procedures shall be submitted to CAF for approval describing the test set-up and the conditions for the noise measurements. In case the saloon HVAC proposed has already been tested previously according to the requirements set below, additional tests may not be needed. In this case, the test report shall be submitted to CAF before the signature of the contract to determine whether additional tests are needed or not. | EFB-RS-118 | Measurements to proof the compliance with the limits set hereafter shall be carried out. Test procedures shall be submitted to CAF for approval describing the test set-up and the conditions for the noise measurements. In case the saloon HVAC proposed has already been tested previously according to the requirements set below, additional tests may not be needed. In this case, the test report shall be submitted to CAF before the signature of the contract to determine whether additional tests are needed or not. | 100 | C |  | C
EFB-RS-119 | All Sound Power Level measurements of the saloon HVAC shall be performed according to the following standard: · ISO 9614-2 | EFB-RS-119 | All Sound Power Level measurements of the saloon HVAC shall be performed according to the following standard: · ISO 9614-2 | 100 | C |  | C
EFB-RS-120 | Sound Pressure Level tests of the saloon HVAC shall be performed, as far as possible, at free field. If this is not feasible and the measurements are performed in an indoors environment, the correction factor per room (K2A) obtained according to the direct method referred in the standard ISO 3744 (section A.3.4) shall be reported. | EFB-RS-120 | Sound Pressure Level tests of the saloon HVAC shall be performed, as far as possible, at free field. If this is not feasible and the measurements are performed in an indoors environment, the correction factor per room (K2A) obtained according to the direct method referred in the standard ISO 3744 (section A.3.4) shall be reported. | 100 | C |  | C
EFB-RS-121 | For the saloon HVAC unit, the following acoustic magnitudes shall be measured: · Acoustic Sound Pressure Level (SPL) · Acoustic Sound Power Level (SWL) | EFB-RS-121 | For the saloon HVAC unit, the following acoustic magnitudes shall be measured: · Acoustic Sound Pressure Level (SPL) · Acoustic Sound Power Level (SWL) | 100 | C |  | C
EFB-RS-122 | For exterior noise, the saloon HVAC shall be tested in cooling mode with the evaporator fan at its lowest speed and in all posssible combinations of refrigeration circuits working (compressor and condenser fan). For interior noise, the supply and return openings shall be tested in ventilation mode, in all possible combinations of evaporator fan speeds. Additionally, tests shall be repeated with the return air damper closed (if applicable) with informative purposes. The supplier shall guarantee that the noise levels required are not exceeded in any of the working points of the evaporator fans (pressure and airflow) needed for this application neither in any of the damper positions (if applicable). For this purpose, the airflow of the evaporator fans shall be adjusted to the expected working points during the noise tests. | EFB-RS-122 | For exterior noise, the saloon HVAC shall be tested in cooling mode with the evaporator fan at its lowest speed and in all posssible combinations of refrigeration circuits working (compressor and condenser fan). For interior noise, the supply and return openings shall be tested in ventilation mode, in all possible combinations of evaporator fan speeds. Additionally, tests shall be repeated with the return air damper closed (if applicable) with informative purposes. The supplier shall guarantee that the noise levels required are not exceeded in any of the working points of the evaporator fans (pressure and airflow) needed for this application neither in any of the damper positions (if applicable). For this purpose, the airflow of the evaporator fans shall be adjusted to the expected working points during the noise tests. | 100 | NC | HC_230517: In the usual procedure measurements are taken from the nominal point and some agree point, not from all possible combinations. | NC | HC_230517: In the usual procedure measurements are taken from the nominal point and some agree point, not from all possible combinations.
EFB-RS-123 | Regarding exterior noise, the sound pressure level of the saloon HVAC unit at every operation condition is to be measured (LpAeq,T): · In a horizontal plane at the height of the HVAC center and 7.5 m away from its center (at the two lateral sides parallel to the train's sidewall). The requirement at 7.5 m shall only be complied with in case this measurement point is available at free field (no recalculation from another distance is permitted). In case it is not, the same measurement shall be done at 1 m away from the equipment surface (at the two lateral sides). | EFB-RS-123 | Regarding exterior noise, the sound pressure level of the saloon HVAC unit at every operation condition is to be measured (LpAeq,T): · In a horizontal plane at the height of the HVAC center and 7.5 m away from its center (at the two lateral sides parallel to the train's sidewall). The requirement at 7.5 m shall only be complied with in case this measurement point is available at free field (no recalculation from another distance is permitted). In case it is not, the same measurement shall be done at 1 m away from the equipment surface (at the two lateral sides). | 100 | C |  | C
EFB-RS-126 | Regarding exterior noise, the Sound Power Level of the saloon HVAC unit at every operation condition is to be measured (LwA): · On the exterior surface. For equipment mounted on top of the roof, the exterior surface sound power measurement must cover the 4 lateral surfaces and the upper surface of the equipment (the condenser fan surface). The distance from the intensity probe to the equipment surface shall never be <100mm. The yellow surface represent the surfaces where the sound power needs to be scanned. | EFB-RS-126 | Regarding exterior noise, the Sound Power Level of the saloon HVAC unit at every operation condition is to be measured (LwA): · On the exterior surface. For equipment mounted on top of the roof, the exterior surface sound power measurement must cover the 4 lateral surfaces and the upper surface of the equipment (the condenser fan surface). The distance from the intensity probe to the equipment surface shall never be <100mm. The yellow surface represent the surfaces where the sound power needs to be scanned. | 100 | C |  | C
EFB-RS-128 | Regarding interior noise, the Sound Power Level of the saloon HVAC unit at every operation condition is to be measured (LwA): · On the air supply openning. Due to the influence of air speed, the air supply openning sound power measurement must be done in an imaginary 5 face parallelepiped where the 6th face is the air supply openning itself. The yellow surface represent the surfaces where the sound power needs to be scanned. The previous measurements shall be made for all supply air opennings that correspond to one evaporator unit together. | EFB-RS-128 | Regarding interior noise, the Sound Power Level of the saloon HVAC unit at every operation condition is to be measured (LwA): · On the air supply openning. Due to the influence of air speed, the air supply openning sound power measurement must be done in an imaginary 5 face parallelepiped where the 6th face is the air supply openning itself. The yellow surface represent the surfaces where the sound power needs to be scanned. The previous measurements shall be made for all supply air opennings that correspond to one evaporator unit together. | 100 | C |  | C
EFB-RS-130 | Regarding interior noise, the Sound Power Level of the saloon HVAC unit at every operation condition is to be measured (LwA): · On the air return openning. The air return openning sound power measurement must be done on the air return openning itself (1 face). In case high air speeds or non-uniform airflows are expected in the return openning , the surfaces to be scanned shall be an imaginary 5 face parallelepiped where the 6th face is the air return openning itself. The yellow surface represent the surfaces where the sound power needs to be scanned. The previous measurements shall be made for all return air opennings that correspond to one evaporator unit together. | EFB-RS-130 | Regarding interior noise, the Sound Power Level of the saloon HVAC unit at every operation condition is to be measured (LwA): · On the air return openning. The air return openning sound power measurement must be done on the air return openning itself (1 face). In case high air speeds or non-uniform airflows are expected in the return openning , the surfaces to be scanned shall be an imaginary 5 face parallelepiped where the 6th face is the air return openning itself. The yellow surface represent the surfaces where the sound power needs to be scanned. The previous measurements shall be made for all return air opennings that correspond to one evaporator unit together. | 100 | C |  | C
EFB-RS-132 | The sound power measurement of the saloon HVAC shall be made without the use of any ducting in the measurement area (yellow the surface). | EFB-RS-132 | The sound power measurement of the saloon HVAC shall be made without the use of any ducting in the measurement area (yellow the surface). | 100 | C |  | C
EFB-RS-136 | For the saloon convector units the following acoustic magnitude shall be measured: · Acoustic Sound Pressure Level (SPL) · Acoustic Sound Power Level (SWL) The supplier shall guarantee that the noise levels required are not exceeded in any of the working points of the convector For this purpose, the airflow of the convector shall be adjusted to the expected working points during the noise tests. | EFB-RS-136 | For the saloon convector units the following acoustic magnitude shall be measured: · Acoustic Sound Pressure Level (SPL) · Acoustic Sound Power Level (SWL) The supplier shall guarantee that the noise levels required are not exceeded in any of the working points of the convector For this purpose, the airflow of the convector shall be adjusted to the expected working points during the noise tests. | 100 | C |  | C
EFB-RS-137 | The sound pressure level of the saloon convector units at every operation condition is to be determined (LpAeq,T): · At 1 m from the equipment surface on the admission side and impulsion side. Note that the convector operation involves fan and resistance operation. | EFB-RS-137 | The sound pressure level of the saloon convector units at every operation condition is to be determined (LpAeq,T): · At 1 m from the equipment surface on the admission side and impulsion side. Note that the convector operation involves fan and resistance operation. | 100 | C |  | C
EFB-RS-138 | The sound pressure level 1 m away from the saloon convector units surfaces on any side will not exceed the value of 58 dBA. In case more than one fan is used in the same convector set, this value applies to both of them together (and not to each of them separately). | EFB-RS-138 | The sound pressure level 1 m away from the saloon convector units surfaces on any side will not exceed the value of 58 dBA. In case more than one fan is used in the same convector set, this value applies to both of them together (and not to each of them separately). | 100 | NC | HC_230517: Taking into account previous similar project solution: - 9422273 underseat Convector (RAMYA project ) 56,8 dBA in impulsion and 61,4 dBA in admision are expected - 9600003 tip up Convector(RAMYA project ) 56,8 dBA in impulsion and 61,4 dBA in admision are expected | NC | HC_230517: Taking into account previous similar project solution: - 9422273 underseat Convector (RAMYA project ) 56,8 dBA in impulsion and 61,4 dBA in admision are expected - 9600003 tip up Convector(RAMYA project ) 56,8 dBA in impulsion and 61,4 dBA in admision are expected
EFB-RS-139 | The Sound Power Level of the saloon convector units at every operation condition is to be measured (LwA): · On the admission surface. The air admission openning sound power measurement must be done on the air admission surface (1 face). The yellow surface represent the surfaces where the sound power needs to be scanned. | EFB-RS-139 | The Sound Power Level of the saloon convector units at every operation condition is to be measured (LwA): · On the admission surface. The air admission openning sound power measurement must be done on the air admission surface (1 face). The yellow surface represent the surfaces where the sound power needs to be scanned. | 100 | C |  | C
EFB-RS-141 | The Sound Power Level of the saloon convector units at every operation condition is to be measured (LwA): · On the supply surface. The air supply openning sound power measurement must be done on the air supply surface (1 face). The yellow surface represent the surfaces where the sound power needs to be scanned. | EFB-RS-141 | The Sound Power Level of the saloon convector units at every operation condition is to be measured (LwA): · On the supply surface. The air supply openning sound power measurement must be done on the air supply surface (1 face). The yellow surface represent the surfaces where the sound power needs to be scanned. | 100 | C |  | C
EFB-RS-143 | The Sound Power Level on the air admission surface of the saloon convector units will not exceed the value of 60 dBA. | EFB-RS-143 | The Sound Power Level on the air admission surface of the saloon convector units will not exceed the value of 60 dBA. | 100 | NC | HC_230517: Taking into account previous similar project solution: - 9422273 underseat Convector (RAMYA project ) 71 dBA are expected - 9600003 tip up Convector(RAMYA project ) 71 dBA are expected | NC | HC_230517: Taking into account previous similar project solution: - 9422273 underseat Convector (RAMYA project ) 71 dBA are expected - 9600003 tip up Convector(RAMYA project ) 71 dBA are expected
EFB-RS-144 | The Sound Power Level on the air supply surface of the saloon convector units will not exceed the value of 60 dBA. | EFB-RS-144 | The Sound Power Level on the air supply surface of the saloon convector units will not exceed the value of 60 dBA. | 100 | C | HC_230517: Taking into account previous similar project solution: - 9422273 underseat Convector (RAMYA project ) 59 dBA are expected - 9600003 tip up Convector(RAMYA project ) 59 dBA are expected | C | HC_230517: Taking into account previous similar project solution: - 9422273 underseat Convector (RAMYA project ) 59 dBA are expected - 9600003 tip up Convector(RAMYA project ) 59 dBA are expected
EFB-RS-145 | The presence of pure tones will be evaluated for the saloon HVAC in accordance to Annex K of the method described in ISO 1996-2:2017 for each test and parameter evaluated, comparing the sound pressure level in the third-octave band of interest with the average of the sound pressure levels of both adjacent third-octave bands. The difference between these values may vary with frequency according the following: · 15 dB in low-frequency bands (25 Hz to 125 Hz) · 8 dB in middle-frequency bands (160 Hz to 400 Hz) · 5 dB in high-frequency bands (500 Hz to 10000 Hz) | EFB-RS-145 | The presence of pure tones will be evaluated for the saloon HVAC in accordance to Annex K of the method described in ISO 1996-2:2017 for each test and parameter evaluated, comparing the sound pressure level in the third-octave band of interest with the average of the sound pressure levels of both adjacent third-octave bands. The difference between these values may vary with frequency according the following: · 15 dB in low-frequency bands (25 Hz to 125 Hz) · 8 dB in middle-frequency bands (160 Hz to 400 Hz) · 5 dB in high-frequency bands (500 Hz to 10000 Hz) | 100 | C |  | C
EFB-RS-146 | If pure tones occur, and the level is less than 10 dBA below the maximum 1/3 octave band level in the spectrum (the band with the highest contribution), 5 dBA will be added to the overall measurement noise value of the saloon HVAC before comparing it to the specified overall limit values of the present specification. | EFB-RS-146 | If pure tones occur, and the level is less than 10 dBA below the maximum 1/3 octave band level in the spectrum (the band with the highest contribution), 5 dBA will be added to the overall measurement noise value of the saloon HVAC before comparing it to the specified overall limit values of the present specification. | 100 | C |  | C
EFB-RS-147 | A saloon HVAC noise test report shall be supplied to CAF for approval which shall include, as a minimum: · Reference to the standard according to which the measurements have been performed · A description of the test set up: - Image of the equipment installation - Description of the instalation environment - Description of fixation points (and description of elastic mountings if necessary) · A description of the measurement points (for SPL) and surfaces (for SWL) · Sound pressure measurements: - Description of the operating conditions for each case and equipment component (evaporator rpm, airflow, number of compressors working, etc.) - The sound pressure measurement results with A frequency weighting - 1/3 octave band analysis of each measurement point for each operating condition (tabulated) for each point - Pass/fail analysis · Sound power measurements: - Description of how sound power is obtained - Description of the operating conditions for each case and equipment component (evaporator rpm, airflow, number of compressors working, etc.) - The sound power measurement results with A frequency weighting - 1/3 octave band analysis of the Sound Power Level for each operating condition (tabulated) for each surface and overall - Pass/fail analysis · Pure tone analysis: - Pass/fail analysis according the Annex K of the method described in ISO 1996-2:2017. Note: Background noise shall be measured. In case the background noise is not 10 dB lower than the noise measured, the corrections shall be done according to the Table 1 of the standard ISO 3095:2005, and shall be documented in the test report. | EFB-RS-147 | A saloon HVAC noise test report shall be supplied to CAF for approval which shall include, as a minimum: · Reference to the standard according to which the measurements have been performed · A description of the test set up: - Image of the equipment installation - Description of the instalation environment - Description of fixation points (and description of elastic mountings if necessary) · A description of the measurement points (for SPL) and surfaces (for SWL) · Sound pressure measurements: - Description of the operating conditions for each case and equipment component (evaporator rpm, airflow, number of compressors working, etc.) - The sound pressure measurement results with A frequency weighting - 1/3 octave band analysis of each measurement point for each operating condition (tabulated) for each point - Pass/fail analysis · Sound power measurements: - Description of how sound power is obtained - Description of the operating conditions for each case and equipment component (evaporator rpm, airflow, number of compressors working, etc.) - The sound power measurement results with A frequency weighting - 1/3 octave band analysis of the Sound Power Level for each operating condition (tabulated) for each surface and overall - Pass/fail analysis · Pure tone analysis: - Pass/fail analysis according the Annex K of the method described in ISO 1996-2:2017. Note: Background noise shall be measured. In case the background noise is not 10 dB lower than the noise measured, the corrections shall be done according to the Table 1 of the standard ISO 3095:2005, and shall be documented in the test report. | 100 | C |  | C
EFB-RS-148 | The supplier shall provide the data sheets that show the noise performance of all the fans (evaporator, condenser, convector and exhaust) for the saloon HVAC equipment. | EFB-RS-148 | The supplier shall provide the data sheets that show the noise performance of all the fans (evaporator, condenser, convector and exhaust) for the saloon HVAC equipment. | 100 | C |  | C
EFB-RS-149 | The saloon HVAC components shall be fixed to their housing by adequate supports to absorve vibrations and to avoid their transmission to the equipment structure. Fixations must be such that the equipment vibrations transmitted to the vehicle are minimized in any of the equipment operation modes up to maximum load. The design process and criteria followed to choose the elastic elements used in the fixations, if any, shall be specified. | EFB-RS-149 | The saloon HVAC components shall be fixed to their housing by adequate supports to absorve vibrations and to avoid their transmission to the equipment structure. Fixations must be such that the equipment vibrations transmitted to the vehicle are minimized in any of the equipment operation modes up to maximum load. The design process and criteria followed to choose the elastic elements used in the fixations, if any, shall be specified. | 100 | C |  | C
EFB-RS-151 | All the equipments shall comply with IEC61373 in all operating conditions. Tests to proof compliance with IEC61373 shall be carried out and the test results shall be submitted to CAF for approval. The following shall be included in the test report: · Boundary conditions · Excitation used and frequency range · Obtained results · Pass/Fail criteria Even if resonaces appear, the limits established in IEC 61373 must be complied with. | EFB-RS-151 | All the equipments shall comply with IEC61373 in all operating conditions. Tests to proof compliance with IEC61373 shall be carried out and the test results shall be submitted to CAF for approval. The following shall be included in the test report: · Boundary conditions · Excitation used and frequency range · Obtained results · Pass/Fail criteria Even if resonaces appear, the limits established in IEC 61373 must be complied with. | 100 | C |  | C
EFB-RS-154 | The average temperature in the Saloon HVAC supply opening shall always be between 12 ºC and 45 ºC, except during preconditioning performance. | EFB-RS-154 | The average temperature in the Saloon HVAC supply opening shall always be between 12 ºC and 45 ºC, except during preconditioning performance. | 100 | C |  | C
EFB-RS-155 | The Saloon HVAC supplier shall determine the internal pressure drops of the HVAC in all operating conditions. The total internal pressure losses should be broken down by components (filters, grids, HVAC geometry, etc.). | EFB-RS-155 | The Saloon HVAC supplier shall determine the internal pressure drops of the HVAC in all operating conditions. The total internal pressure losses should be broken down by components (filters, grids, HVAC geometry, etc.). | 100 | C |  | C
EFB-RS-158 | The Saloon HVAC supplier shall deliver the load calculation in the required conditions. Each calculation should be broken down in the following sections: trasmission, occupation, solar load, air renewal and internal loads (lights, electrical cabinets and internal HVAC loads). Sensible and latent heat loads should be separated in coolig calculations. | EFB-RS-158 | The Saloon HVAC supplier shall deliver the load calculation in the required conditions. Each calculation should be broken down in the following sections: trasmission, occupation, solar load, air renewal and internal loads (lights, electrical cabinets and internal HVAC loads). Sensible and latent heat loads should be separated in coolig calculations. | 100 | C |  | C
EFB-RS-159 | The Saloon HVAC unit power calculation, in cooling mode, shall be carried out with a static K-value of 1.6 W/m²K | EFB-RS-159 | The Saloon HVAC unit power calculation, in cooling mode, shall be carried out with a static K-value of 1.6 W/m²K | 100 | C |  | C
EFB-RS-160 | The Saloon HVAC unit power calculation, in heating mode, shall be carried out with a dynamic K-value of 2.2 W/m²K | EFB-RS-160 | The Saloon HVAC unit power calculation, in heating mode, shall be carried out with a dynamic K-value of 2.2 W/m²K | 100 | C |  | C
EFB-RS-161 | The precooling time shall be calculated with a inertia of 40 KJ/m3K in the saloon. | EFB-RS-161 | The precooling time shall be calculated with a inertia of 40 KJ/m3K in the saloon. | 100 | C |  | C
EFB-RS-162 | The preheating time shall be calculated with a inertia of 40 KJ/m3K in the saloon. | EFB-RS-162 | The preheating time shall be calculated with a inertia of 40 KJ/m3K in the saloon. | 100 | C |  | C
EFB-RS-164 | The Saloon HVAC unit power calculations shall be calculated with an absorbance value of 0.8 for the roof and sidewall | EFB-RS-164 | The Saloon HVAC unit power calculations shall be calculated with an absorbance value of 0.8 for the roof and sidewall | 100 | C |  | C
EFB-RS-165 | The Saloon HVAC unit power calculation, in cooling mode, shall be calculated with an external convection value of 15W/m2K | EFB-RS-165 | The Saloon HVAC unit power calculation, in cooling mode, shall be calculated with an external convection value of 15W/m2K | 100 | C |  | C
EFB-RS-166 | The Saloon HVAC unit power calculation, in cooling mode, shall be calculated with a 100% of exposure to the sun | EFB-RS-166 | The Saloon HVAC unit power calculation, in cooling mode, shall be calculated with a 100% of exposure to the sun | 100 | C |  | C
EFB-RS-167 | The saloon convector supply temperature shall always be below 45ºC, excecpt in preheating, with a pressure drop of the 50 Pa of the ducts | EFB-RS-167 | The saloon convector supply temperature shall always be below 45ºC, excecpt in preheating, with a pressure drop of the 50 Pa of the ducts | 100 | C | HC_230517: C for 45ºC calculated as average value in saloon convector the temperature air distribution in convector air outlet is always variable, due to the convector construcction (mainly for the electrical resistences geometry). so is not possible to assure less tahn 45ºC in every points, only the average. HISPACOLD trabajará conjuntamente con CAF para que la temperatura de impulsión de los convectores cumpla con la normativa EN14750 & EN14813. | C | HC_230517: C for 45ºC calculated as average value in saloon convector the temperature air distribution in convector air outlet is always variable, due to the convector construcction (mainly for the electrical resistences geometry). so is not possible to assure less tahn 45ºC in every points, only the average. HISPACOLD trabajará conjuntamente con CAF para que la temperatura de impulsión de los convectores cumpla con la normativa EN14750 & EN14813.
EFB-RS-168 | The ducting of the STD WC shall be designed to supply 100 m3/h | EFB-RS-168 | The ducting of the STD WC shall be designed to supply 100 m3/h | 100 | NA |  | NA
EFB-RS-169 | The extraction system of the STD WC shall be designed to extract at least 100 m3/h@ for a presure load of 100Pa. | EFB-RS-169 | The extraction system of the STD WC shall be designed to extract at least 100 m3/h@ for a presure load of 100Pa. | 100 | NA | HC_230517: Extraction WC system not defined in this specification under HC scope of supply | NA | HC_230517: Extraction WC system not defined in this specification under HC scope of supply
EFB-RS-171 | Start-up overcurrent (in-rush) and overvoltage data shall be provided by supplier as well as the power consumption in normal mode and standby for AC and DC. | EFB-RS-171 | Start-up overcurrent (in-rush) and overvoltage data shall be provided by supplier as well as the power consumption in normal mode and standby for AC and DC. | 100 | C |  | C
EFB-RS-172 | The nominal output voltage of the fixed frequency AC power supply for general loads will be 3 * 400 Vac; Freq= 50Hz (acc. EN50533 and IEC60077) | EFB-RS-172 | The nominal output voltage of the fixed frequency AC power supply for general loads will be 3 * 400 Vac; Freq= 50Hz (acc. EN50533 and IEC60077) | 100 | C |  | C
EFB-RS-173 | In the case the neutral is required by the system, please declare. | EFB-RS-173 | In the case the neutral is required by the system, please declare. | 100 | C |  | C
EFB-RS-174 | DC outputs characteristics: • Nominal Voltage: 110VDC +25/-30% • other specifications according to EN50155:2017 | EFB-RS-174 | DC outputs characteristics: • Nominal Voltage: 110VDC +25/-30% • other specifications according to EN50155:2017 | 100 | C |  | C
EFB-RS-175 | If any kind of internal battery is used, low voltage warning shall be provided. | EFB-RS-175 | If any kind of internal battery is used, low voltage warning shall be provided. | 100 | C |  | C
EFB-RS-176 | The System shall incorporate its own electrical protections (polarity surges, polarity inversion, over- and subvoltage, short circuit and phase loss among others). | EFB-RS-176 | The System shall incorporate its own electrical protections (polarity surges, polarity inversion, over- and subvoltage, short circuit and phase loss among others). | 100 | C |  | C
EFB-RS-177 | All live parts shall be protected. Protection can be achieved either by panels or voltage discharging devices in each access point. These panels and devices will be supported by labels appropriate to the location. EN 50153 and EN 50124-1-2 requirements sh | EFB-RS-177 | All live parts shall be protected. Protection can be achieved either by panels or voltage discharging devices in each access point. These panels and devices will be supported by labels appropriate to the location. EN 50153 and EN 50124-1-2 requirements sh | 100 | C |  | C
EFB-RS-178 | All components must be properly earth connected. Number and arrangement of these connecting points will be approved by CAF. The supporting elements cannot be used as earthing contacts. | EFB-RS-178 | All components must be properly earth connected. Number and arrangement of these connecting points will be approved by CAF. The supporting elements cannot be used as earthing contacts. | 100 | C |  | C
EFB-RS-179 | Circuit breakers with auxiliary contacts (nominal current not lower than 4 A) shall be used. | EFB-RS-179 | Circuit breakers with auxiliary contacts (nominal current not lower than 4 A) shall be used. | 100 | C |  | C
EFB-RS-180 | Fuses are not allowed for protection. Exceptions shall be declared by supplier and approved by CAF. | EFB-RS-180 | Fuses are not allowed for protection. Exceptions shall be declared by supplier and approved by CAF. | 100 | C |  | C
EFB-RS-181 | Electrical and electronic parts, which are connected to circuits by plugs and which are not interchangeable in terms of their circuit functions, shall be provided with a suitable means to prevent them from being inserted incorrectly or in the wrong position. The equipment shall be clearly labelled. | EFB-RS-181 | Electrical and electronic parts, which are connected to circuits by plugs and which are not interchangeable in terms of their circuit functions, shall be provided with a suitable means to prevent them from being inserted incorrectly or in the wrong position. The equipment shall be clearly labelled. | 100 | C |  | C
EFB-RS-182 | IEC-60571 standard must also be complied (Electronic Equipment used on Rail Vehicles) | EFB-RS-182 | IEC-60571 standard must also be complied (Electronic Equipment used on Rail Vehicles) | 100 | NA |  | NA
EFB-RS-183 | Digital Input/outputs will perform with train battery voltage. | EFB-RS-183 | Digital Input/outputs will perform with train battery voltage. | 100 | C | HC_230517: A DC/DC converter is used internally | C | HC_230517: A DC/DC converter is used internally
EFB-RS-184 | Input channels faults shall not produce any output effects (isolation). | EFB-RS-184 | Input channels faults shall not produce any output effects (isolation). | 100 | C |  | C
EFB-RS-185 | Equipment shall be tested for vibration and shock in accordance with the requirements of EN 50155. | EFB-RS-185 | Equipment shall be tested for vibration and shock in accordance with the requirements of EN 50155. | 100 | C |  | C
EFB-RS-186 | Specific measures shall be put in place to protect electronic equipment, its control logics, SW, memories, processors, etc., against the power supply voltage cut, whether it is controlled shutdowns, or sudden or untimely shutdowns. All sensitive equipment will have internal batteries, UPSs, or the necessary items for this protection.. | EFB-RS-186 | Specific measures shall be put in place to protect electronic equipment, its control logics, SW, memories, processors, etc., against the power supply voltage cut, whether it is controlled shutdowns, or sudden or untimely shutdowns. All sensitive equipment will have internal batteries, UPSs, or the necessary items for this protection.. | 100 | C |  | C
EFB-RS-187 | All on-board equipment shall provide a declaration of conformity in accordance with the EMC Directive 2014/30/EU | EFB-RS-187 | All on-board equipment shall provide a declaration of conformity in accordance with the EMC Directive 2014/30/EU | 100 | C |  | C
EFB-RS-188 | All on-board equipment shall comply the requirements in the standard EN 50121-3-2:2016 | EFB-RS-188 | All on-board equipment shall comply the requirements in the standard EN 50121-3-2:2016 | 100 | C |  | C
EFB-RS-189 | All on-board equipment shall provide a test report or a test certificate to demonstrate compliance with the requirements in the standard EN 50121-3-2:2016 | EFB-RS-189 | All on-board equipment shall provide a test report or a test certificate to demonstrate compliance with the requirements in the standard EN 50121-3-2:2016 | 100 | C |  | C
EFB-RS-190 | The heating equipment shall be fitted with a device to protect it from abnormal increases in air and equipment temperature. The activation of this safety device shall isolate the heater as is required by EN 13129-1:2002 (9.6.1). | EFB-RS-190 | The heating equipment shall be fitted with a device to protect it from abnormal increases in air and equipment temperature. The activation of this safety device shall isolate the heater as is required by EN 13129-1:2002 (9.6.1). | 100 | C |  | C
EFB-RS-191 | The HVAC's cooling system shall include a device in order to prevent overpressure of the refrigerant fluid. This requirement applies to the HVAC of the saloon and the cab. | EFB-RS-191 | The HVAC's cooling system shall include a device in order to prevent overpressure of the refrigerant fluid. This requirement applies to the HVAC of the saloon and the cab. | 100 | C |  | C
EFB-RS-193 | The Supplier shall be responsible for the design, power supply, monitoring and control as well as for the appropriate components for the Saloon HVAC System and for the correct operation thereof once mounted on the units. | EFB-RS-193 | The Supplier shall be responsible for the design, power supply, monitoring and control as well as for the appropriate components for the Saloon HVAC System and for the correct operation thereof once mounted on the units. | 100 | C |  | C
EFB-RS-196 | The offer shall indicate the complete Scope of Supply of the offered system. It shall include, as a minimum, all the elements and devices required and described along this specification. | EFB-RS-196 | The offer shall indicate the complete Scope of Supply of the offered system. It shall include, as a minimum, all the elements and devices required and described along this specification. | 100 | C |  | C
EFB-RS-197 | The Supplier shall provide during the tender stage references of applications of the proposed solution or similar ones. | EFB-RS-197 | The Supplier shall provide during the tender stage references of applications of the proposed solution or similar ones. | 100 | C |  | C
EFB-RS-201 | The heating function of the passenger climate control system shall be supported by a combination of overhead heat and floor heat. The overhead heat shall be provided by the electric overhead heaters. The floor heat shall be provided by floor heat convectors. | EFB-RS-201 | The heating function of the passenger climate control system shall be supported by a combination of overhead heat and floor heat. The overhead heat shall be provided by the electric overhead heaters. The floor heat shall be provided by floor heat convectors. | 100 | C |  | C
EFB-RS-202 | The HVAC units will be identical and interchangeable with others HVAC of different cars. | EFB-RS-202 | The HVAC units will be identical and interchangeable with others HVAC of different cars. | 100 | C |  | C
EFB-RS-203 | The Saloon HVAC system including floor heating solution shall be specially designed for rail application, whereby their components must meet all the required standards regarding electronic construction, vibration levels etc. | EFB-RS-203 | The Saloon HVAC system including floor heating solution shall be specially designed for rail application, whereby their components must meet all the required standards regarding electronic construction, vibration levels etc. | 100 | NC | HC_230517: Vibration tests for convectors not considered initially, according to previus projects. A conformity declaration of service proven could be provide. And also a offer as option could be provided in the economical offer. | NC | HC_230517: Vibration tests for convectors not considered initially, according to previus projects. A conformity declaration of service proven could be provide. And also a offer as option could be provided in the economical offer.
EFB-RS-204 | The HVAC system shall reliably and efficiently control internal environmental parameters, such that all Passengers are provided with a clean and comfortable environment throughout the range of climatic conditions experienced on the line and all air pollution conditions encountered all along the route that is partially in the open air and partially inside tunnels. The climate installation shall guarantee a comfortable climate as energy efficiently as possible. | EFB-RS-204 | The HVAC system shall reliably and efficiently control internal environmental parameters, such that all Passengers are provided with a clean and comfortable environment throughout the range of climatic conditions experienced on the line and all air pollution conditions encountered all along the route that is partially in the open air and partially inside tunnels. The climate installation shall guarantee a comfortable climate as energy efficiently as possible. | 100 | C |  | C
EFB-RS-205 | The HVAC System shall be installed on each car to provide full control of interior temperatures automatically, over the full range of heat loads associated with passengers, miscellaneous electrical equipment, lighting, heat transmission, infiltrations because of frequent opening/closing of doors and solar gain. | EFB-RS-205 | The HVAC System shall be installed on each car to provide full control of interior temperatures automatically, over the full range of heat loads associated with passengers, miscellaneous electrical equipment, lighting, heat transmission, infiltrations because of frequent opening/closing of doors and solar gain. | 100 | C |  | C
EFB-RS-206 | The cabs will be equipped with equipment that is independent of the HVAC that is in the compartment (separated functionally and physically). Additionally, if the cab equipment fails, there is a duct that can be opened and closed manually that will supply air from the general climate control equipment of the passenger car. | EFB-RS-206 | The cabs will be equipped with equipment that is independent of the HVAC that is in the compartment (separated functionally and physically). Additionally, if the cab equipment fails, there is a duct that can be opened and closed manually that will supply air from the general climate control equipment of the passenger car. | 100 | NA | HC_230517: Out of scope of supply and definition of HC | NA | HC_230517: Out of scope of supply and definition of HC
EFB-RS-207 | The HVAC unit will be powered from the auxiliary power unit, at 400VAC 50Hz 3 phase | EFB-RS-207 | The HVAC unit will be powered from the auxiliary power unit, at 400VAC 50Hz 3 phase | 100 | C |  | C
EFB-RS-208 | The electronic controller and the evaporator fans will be powered from 110 VDC power. In case 400 VAC power is selected for evaporator fans, an electrical inverter shall be included inside HVAC unit in order to supply evaporator motors with 400VAC from the 110 VDC provided from train battery, in order to allow emergency ventilation. | EFB-RS-208 | The electronic controller and the evaporator fans will be powered from 110 VDC power. In case 400 VAC power is selected for evaporator fans, an electrical inverter shall be included inside HVAC unit in order to supply evaporator motors with 400VAC from the 110 VDC provided from train battery, in order to allow emergency ventilation. | 100 | C | HC_230517: A 110 VDC evaporator fan model is considered | C | HC_230517: A 110 VDC evaporator fan model is considered
EFB-RS-209 | Service proven in railroad operation systems and components are required (or equivalents). References are required in offer stage. | EFB-RS-209 | Service proven in railroad operation systems and components are required (or equivalents). References are required in offer stage. | 100 | C |  | C
EFB-RS-210 | The Supplier will provide during the tender stage a comprehensive list of which standards are proposed to be complied with for each of the aspects to be considered in the design of the HVAC, the air distribution and the testing of the HVAC unit separately and already installed in the car. | EFB-RS-210 | The Supplier will provide during the tender stage a comprehensive list of which standards are proposed to be complied with for each of the aspects to be considered in the design of the HVAC, the air distribution and the testing of the HVAC unit separately and already installed in the car. | 100 | C |  | C
EFB-RS-211 | The Supplier shall submit the system design supported by technical and functional description, schematic layouts, equipment sizing and selection, airflow distributions, cooling load estimation and psychometric charts to meet the saloon environmental requirements including, but not be limited to, temperature, relative humidity and noise requirements. | EFB-RS-211 | The Supplier shall submit the system design supported by technical and functional description, schematic layouts, equipment sizing and selection, airflow distributions, cooling load estimation and psychometric charts to meet the saloon environmental requirements including, but not be limited to, temperature, relative humidity and noise requirements. | 100 | C | HC_230517: All this documentation will be provided in the project phase | C | HC_230517: All this documentation will be provided in the project phase
EFB-RS-214 | The HVAC system for passenger areas shall be designed in order to fulfill all the thermal requirements defined in Section 3.1 Performance. | EFB-RS-214 | The HVAC system for passenger areas shall be designed in order to fulfill all the thermal requirements defined in Section 3.1 Performance. | 100 | C |  | C
EFB-RS-215 | The air conditioning system must counteract any fast pressure variations when running through tunnels or passing on-coming trains. | EFB-RS-215 | The air conditioning system must counteract any fast pressure variations when running through tunnels or passing on-coming trains. | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-217 | Solutions used to counteract these fast pressure variations must not be noisy. Systems for mitigating pressure variations shall to the greatest extent possible work preventively so that passengers experience pressure changes inside the train to the least extent possible. | EFB-RS-217 | Solutions used to counteract these fast pressure variations must not be noisy. Systems for mitigating pressure variations shall to the greatest extent possible work preventively so that passengers experience pressure changes inside the train to the least extent possible. | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-218 | The Unit indoor pressure variation will be compliant with the requirements specified in anex B3 of EN14067-5. | EFB-RS-218 | The Unit indoor pressure variation will be compliant with the requirements specified in anex B3 of EN14067-5. | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER. Additionally: From the scope of standard: "This document establishes aerodynamic requirements, test procedures, assessment methods and acceptance criteria for operating rolling stock in tunnels. Aerodynamic pressure variations, loads, micro pressure wave generation and further aerodynamic aspects to be expected in tunnel operation are addressed in this document. Requirements for the aerodynamic design of rolling stock and tunnels of the heavy rail system are provided. The requirements apply to heavy rail systems only" | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER. Additionally: From the scope of standard: "This document establishes aerodynamic requirements, test procedures, assessment methods and acceptance criteria for operating rolling stock in tunnels. Aerodynamic pressure variations, loads, micro pressure wave generation and further aerodynamic aspects to be expected in tunnel operation are addressed in this document. Requirements for the aerodynamic design of rolling stock and tunnels of the heavy rail system are provided. The requirements apply to heavy rail systems only"
EFB-RS-219 | The Supplier will confirm during the tender stage if instead of fitting an electric fresh air damper additionally to the pneumatic fresh air damper, the required regulation of the fresh airflow depending on the passenger load could be provided with a return air damper with opening regulation. | EFB-RS-219 | The Supplier will confirm during the tender stage if instead of fitting an electric fresh air damper additionally to the pneumatic fresh air damper, the required regulation of the fresh airflow depending on the passenger load could be provided with a return air damper with opening regulation. | 100 | C | HC_230517: the base proposal not included a pneumatic damper. The solution proposed is based in a single damper actuator for air fresh inlet, in charge of Fresh air inlets regulation and aditional single damper actuator ro return air inlet, in charge of return air flow regulation. | C | HC_230517: the base proposal not included a pneumatic damper. The solution proposed is based in a single damper actuator for air fresh inlet, in charge of Fresh air inlets regulation and aditional single damper actuator ro return air inlet, in charge of return air flow regulation.
EFB-RS-220 | The HVAC unit shall be rated to operate at different conditions, defined in "Calculations to perform SALOON" datasheet. The Supplier will dimension and design the HVAC unit in order to provide a good regulation capability and to comply with all the required performances in all the defined conditions. | EFB-RS-220 | The HVAC unit shall be rated to operate at different conditions, defined in "Calculations to perform SALOON" datasheet. The Supplier will dimension and design the HVAC unit in order to provide a good regulation capability and to comply with all the required performances in all the defined conditions. | 100 | C |  | C
EFB-RS-221 | The Supplier will collaborate with CAF in the design of the ducting and the location of the sensors and thermostats in order to comply with the maximum temperature variation in the sections above in any working condition. | EFB-RS-221 | The Supplier will collaborate with CAF in the design of the ducting and the location of the sensors and thermostats in order to comply with the maximum temperature variation in the sections above in any working condition. | 100 | C |  | C
EFB-RS-222 | The Supplier will propose the minimum supply airflow per HVAC unit to consider for this project, in order to reduce the pressure losses in the air ducts. The supply airflow will be maintained constant for all the conditions. | EFB-RS-222 | The Supplier will propose the minimum supply airflow per HVAC unit to consider for this project, in order to reduce the pressure losses in the air ducts. The supply airflow will be maintained constant for all the conditions. | 100 | C |  | C
EFB-RS-223 | The temperature shall be recovered to the nominal after a door opening/closing sequence. Consider a usual cycle of doors opening/ closing as in the EN14750-1. The Supplier will explain during the tender stage how this effect is considered in the calculations and in the regulation. | EFB-RS-223 | The temperature shall be recovered to the nominal after a door opening/closing sequence. Consider a usual cycle of doors opening/ closing as in the EN14750-1. The Supplier will explain during the tender stage how this effect is considered in the calculations and in the regulation. | 100 | C |  | C
EFB-RS-225 | Control system must be able to cope with rapid change in outside temperature conditions when train is entering/leaving tunnels with inside air temperature higher than ambient temperature. | EFB-RS-225 | Control system must be able to cope with rapid change in outside temperature conditions when train is entering/leaving tunnels with inside air temperature higher than ambient temperature. | 100 | C |  | C
EFB-RS-226 | The Supplier will confirm during the tender stage the number of stages considered in the fresh airflow regulation. This number will not be lower than 4. | EFB-RS-226 | The Supplier will confirm during the tender stage the number of stages considered in the fresh airflow regulation. This number will not be lower than 4. | 100 | C |  | C
EFB-RS-230 | A loads analysis of the car body thermal parameters and equipment and passenger loads shall be performed during the tender stage, supporting the proposed HVAC system capacity. | EFB-RS-230 | A loads analysis of the car body thermal parameters and equipment and passenger loads shall be performed during the tender stage, supporting the proposed HVAC system capacity. | 100 | C |  | C
EFB-RS-231 | The load analysis will include at least all the calculations required in the sheet "Calculations to perform SALOON". The supplier will fill all the empty cells of the table (cells in yellow and blue), and will propose the cooling and heating power required in order to safely provide the required performances. | EFB-RS-231 | The load analysis will include at least all the calculations required in the sheet "Calculations to perform SALOON". The supplier will fill all the empty cells of the table (cells in yellow and blue), and will propose the cooling and heating power required in order to safely provide the required performances. | 100 | C |  | C
EFB-RS-232 | The Supplier shall include the value of the supply air temperature in all the thermal calculations. | EFB-RS-232 | The Supplier shall include the value of the supply air temperature in all the thermal calculations. | 100 | C |  | C
EFB-RS-233 | The Supplier will include the condensing temperature in the thermal calculations. | EFB-RS-233 | The Supplier will include the condensing temperature in the thermal calculations. | 100 | C |  | C
EFB-RS-234 | The Supplier will be responsible of identifying if there is other more demanding condition to consider in the calculations, in order to dimension correctly all the components in the HVAC unit. In case there is any, the Supplier will include the new conditions in the "Calculations to perform SALOON" datasheet and will consider also these conditions as design conditions. | EFB-RS-234 | The Supplier will be responsible of identifying if there is other more demanding condition to consider in the calculations, in order to dimension correctly all the components in the HVAC unit. In case there is any, the Supplier will include the new conditions in the "Calculations to perform SALOON" datasheet and will consider also these conditions as design conditions. | 100 | C |  | C
EFB-RS-235 | The Supplier will confirm during the tender stage if the Reheat mode is necessary. | EFB-RS-235 | The Supplier will confirm during the tender stage if the Reheat mode is necessary. | 100 | NA | HC_230517: Not considered initially. HC justify that the humidity value is reached due to load stimation of latent and sensible in calculations. Due to consideering the most restricting condiction (Full passengers) the equipment will be sure that the standard humidity level inside is over get. HC has not require in former project to include humidity sensor and has never regulate according to this. Reheat function has been used only to defrog the front window. | NA | V0: PROY_XX HC_230517: Not considered initially. HC justify that the humidity value is reached due to load stimation of latent and sensible in calculations. Due to consideering the most restricting condiction (Full passengers) the equipment will be sure that the standard humidity level inside is over get. HC has not require in former project to include humidity sensor and has never regulate according to this. Reheat function has been used only to defrog the front window.
EFB-RS-236 | The Supplier will confirm during the tender stage the high extreme temperature the HVAC system can be running at full cooling mode. This temperature will not be lower than 55ºC. The Supplier will confirm the maximum temperature the HVAC system can be running at modulated mode. | EFB-RS-236 | The Supplier will confirm during the tender stage the high extreme temperature the HVAC system can be running at full cooling mode. This temperature will not be lower than 55ºC. The Supplier will confirm the maximum temperature the HVAC system can be running at modulated mode. | 100 | C |  | C
EFB-RS-237 | The Supplier shall provide during the tender stage and accurate and detailed calculation of the power consumption (kW and kVA) of the complete scope of supply of the HVAC system for all the operation modes. The AC and DC power consumption analysis will include at least all the calculations required in the sheet "Electric Power Consumpt. SALOON". The supplier will fill all the empty cells of the table (cells in yellow), considering the maximum tolerances of each component. None additional tolerances shall be accepted. For the Supply air fan the supplier will fill the power values in the AC or DC cells, as applicable, not in both. | EFB-RS-237 | The Supplier shall provide during the tender stage and accurate and detailed calculation of the power consumption (kW and kVA) of the complete scope of supply of the HVAC system for all the operation modes. The AC and DC power consumption analysis will include at least all the calculations required in the sheet "Electric Power Consumpt. SALOON". The supplier will fill all the empty cells of the table (cells in yellow), considering the maximum tolerances of each component. None additional tolerances shall be accepted. For the Supply air fan the supplier will fill the power values in the AC or DC cells, as applicable, not in both. | 100 | C |  | C
EFB-RS-238 | The Supplier shall provide during the tender stage the inrush current values of the proposed equipment. | EFB-RS-238 | The Supplier shall provide during the tender stage the inrush current values of the proposed equipment. | 100 | C |  | C
EFB-RS-239 | The specific proposals to minimise energy consumption of the HVAC unit shall be detailed in the tender. The Supplier will explain not only the concept but will also estimate the energy reduction considered for each of the proposed solutions. The supplier will estimate at tender stage for exterior maximum temperature with full cooling capacity the COP value. Please specify the COP value and the conditions. COP will be higher than 2. | EFB-RS-239 | The specific proposals to minimise energy consumption of the HVAC unit shall be detailed in the tender. The Supplier will explain not only the concept but will also estimate the energy reduction considered for each of the proposed solutions. The supplier will estimate at tender stage for exterior maximum temperature with full cooling capacity the COP value. Please specify the COP value and the conditions. COP will be higher than 2. | 100 | C |  | C
EFB-RS-240 | The Supplier will calculate during the tender stage the fresh/recycled air ratio according to an applicable standard and will explain the criteria considered for this calculation. | EFB-RS-240 | The Supplier will calculate during the tender stage the fresh/recycled air ratio according to an applicable standard and will explain the criteria considered for this calculation. | 100 | C |  | C
EFB-RS-241 | The AC or DC power demand due to the HVAC system's ventilation mode shall be specified. | EFB-RS-241 | The AC or DC power demand due to the HVAC system's ventilation mode shall be specified. | 100 | C |  | C
EFB-RS-242 | The AC energy consumption values due to the HVAC system shall be verified. | EFB-RS-242 | The AC energy consumption values due to the HVAC system shall be verified. | 100 | C |  | C
EFB-RS-244 | The location of the Temperature sensors will be defined during the project stage. They will not be unduly influenced by local sources of heat, such as motors or resistors, or the fresh air stream. | EFB-RS-244 | The location of the Temperature sensors will be defined during the project stage. They will not be unduly influenced by local sources of heat, such as motors or resistors, or the fresh air stream. | 100 | C |  | C
EFB-RS-245 | Sensors shall be protected from accidental damage. | EFB-RS-245 | Sensors shall be protected from accidental damage. | 100 | C |  | C
EFB-RS-246 | Each HVAC system will be fitted with a filter distribution for a proper operation of the HVAC equipment. The temperature values will be available in the communication bus. | EFB-RS-246 | Each HVAC system will be fitted with a filter distribution for a proper operation of the HVAC equipment. The temperature values will be available in the communication bus. | 100 | C |  | C
EFB-RS-247 | One supply air temperature sensor per HVAC system shall be also included inside the HVAC unit. | EFB-RS-247 | One supply air temperature sensor per HVAC system shall be also included inside the HVAC unit. | 100 | C |  | C
EFB-RS-249 | Provision to shut off the fresh air intake and re-circulate the internal air of the saloon, during an emergency condition, such as fire outside the train is required in this application. | EFB-RS-249 | Provision to shut off the fresh air intake and re-circulate the internal air of the saloon, during an emergency condition, such as fire outside the train is required in this application. | 100 | C |  | C
EFB-RS-250 | In case of fault in the power supply the fresh air damper, and the quick pneumatic actuation damper shall remain open as to intake the maximum fresh airflow. | EFB-RS-250 | In case of fault in the power supply the fresh air damper, and the quick pneumatic actuation damper shall remain open as to intake the maximum fresh airflow. | 100 | C | HC_200517: With the current approach agreed, a electrical actuator will be provided for fresh air inlet and return air inlet, so, with this aproach, understanding "power failure" as loss of 400 VAC supply, the answer would be C. In case of loss of 110 VDC, The evaporator fan and the damper are powered at 110 VDC. The fresh air damper will be closed only in preconditioning modes or emergency/fire conditions, only in this case, if 110 Vdc fails the damper will rest in this position. In normal operation the damper will be open in case of faliure of 110 VDC. | C | HC_200517: With the current approach agreed, a electrical actuator will be provided for fresh air inlet and return air inlet, so, with this aproach, understanding "power failure" as loss of 400 VAC supply, the answer would be C. In case of loss of 110 VDC, The evaporator fan and the damper are powered at 110 VDC. The fresh air damper will be closed only in preconditioning modes or emergency/fire conditions, only in this case, if 110 Vdc fails the damper will rest in this position. In normal operation the damper will be open in case of faliure of 110 VDC.
EFB-RS-251 | Return air dampers shall be provided if they enable a big reduction in the electric power consumption during the emergency ventilation condition. In case they are fitted, these dampers will be included inside the HVAC unit. | EFB-RS-251 | Return air dampers shall be provided if they enable a big reduction in the electric power consumption during the emergency ventilation condition. In case they are fitted, these dampers will be included inside the HVAC unit. | 100 | C | HC_230517: the HVAC will have a return damper to regulate the different rates of fresh air. Only with fresh air damper it is not possible get its. | C | HC_230517: the HVAC will have a return damper to regulate the different rates of fresh air. Only with fresh air damper it is not possible get its.
EFB-RS-252 | The Supplier shall provide references of previous applications of the fresh and return air dampers during the tender stage, and the times required to pass from a completely closed position to a completely open position. | EFB-RS-252 | The Supplier shall provide references of previous applications of the fresh and return air dampers during the tender stage, and the times required to pass from a completely closed position to a completely open position. | 100 | C | HC_230517: Return: 35 seconds to 90º Fresh air: 35 seconds to 90º | C | HC_230517: Return: 35 seconds to 90º Fresh air: 35 seconds to 90º
EFB-RS-253 | The actuators of the dampers shall be highly reliable and shall be metallic and shall provide an accurate control of the opening position. | EFB-RS-253 | The actuators of the dampers shall be highly reliable and shall be metallic and shall provide an accurate control of the opening position. | 100 | NC | HC_230517: The actuator is considered and used as standard. Belimo actuator is the one used in previous projects in service. This actuator has plastic compenents. These will be declared in Fire & Smoke declaration to be send for milestone 2. | NC | HC_230517: The actuator is considered and used as standard. Belimo actuator is the one used in previous projects in service. This actuator has plastic compenents. These will be declared in Fire & Smoke declaration to be send for milestone 2.
EFB-RS-254 | Each HVAC unit shall be arranged on an integral frame, removable from the car as a single complete module. The integral frame housing of the unit shall be constructed such that to avoid any corrosion in service on any account and the box shall last for the lifetime of the HVAC unit without needing any attention. | EFB-RS-254 | Each HVAC unit shall be arranged on an integral frame, removable from the car as a single complete module. The integral frame housing of the unit shall be constructed such that to avoid any corrosion in service on any account and the box shall last for the lifetime of the HVAC unit without needing any attention. | 100 | C |  | C
EFB-RS-255 | All the electrical connectors will be suitable for railways application and should be fitted with a mechanical lock. | EFB-RS-255 | All the electrical connectors will be suitable for railways application and should be fitted with a mechanical lock. | 100 | C |  | C
EFB-RS-256 | All external grilles shall be designed to protect the coil face as well as prevent snow, frost and water ingress resulting from adverse weather or train washing. The Supplier will define the material of the external grilles during the tender stage. | EFB-RS-256 | All external grilles shall be designed to protect the coil face as well as prevent snow, frost and water ingress resulting from adverse weather or train washing. The Supplier will define the material of the external grilles during the tender stage. | 100 | C |  | C
EFB-RS-257 | The Supplier will optimize the design of the external grilles to be used in the condenser and in the evaporator area as to avoid the bypass of the hot air from the condenser coming into the fresh air inlet. | EFB-RS-257 | The Supplier will optimize the design of the external grilles to be used in the condenser and in the evaporator area as to avoid the bypass of the hot air from the condenser coming into the fresh air inlet. | 100 | C |  | C
EFB-RS-258 | The HVAC system will provide following operational modes: • OFF mode • ON-normal mode with the following states of activity: - Pre-heating/pre-cooling mode - Ventilation mode - Cooling mode - Heating mode • Special modes - Degraded mode - Emergency mode - Maximum renovation mode Additional modes could be proposed. • Testing mode The selection of operating modes desired is effected via bus inputs from train system. | EFB-RS-258 | The HVAC system will provide following operational modes: • OFF mode • ON-normal mode with the following states of activity: - Pre-heating/pre-cooling mode - Ventilation mode - Cooling mode - Heating mode • Special modes - Degraded mode - Emergency mode - Maximum renovation mode Additional modes could be proposed. • Testing mode The selection of operating modes desired is effected via bus inputs from train system. | 100 | C | HC_230517: to be discussed and agreed during the development of the project. Usually some other modes are necessary as well. | C | HC_230517: to be discussed and agreed during the development of the project. Usually some other modes are necessary as well.
EFB-RS-259 | The pre-conditioning mode will be automatically initiated via the HVAC controller depending on the temperature difference between interior temperature and the interior set point. Pre-conditioning mode includes both pre-heating and pre-cooling modes. The air conditioning system will finish preconditioning mode if the following circumstance occurs: The CO2 concentration measured by the sensor exceeds 1000ppm (TBD). Exceeding this limit would mean the presence of passengers in the room, so the HVAC would work in Cooling/Heating mode to allow the entry of fresh air. | EFB-RS-259 | The pre-conditioning mode will be automatically initiated via the HVAC controller depending on the temperature difference between interior temperature and the interior set point. Pre-conditioning mode includes both pre-heating and pre-cooling modes. The air conditioning system will finish preconditioning mode if the following circumstance occurs: The CO2 concentration measured by the sensor exceeds 1000ppm (TBD). Exceeding this limit would mean the presence of passengers in the room, so the HVAC would work in Cooling/Heating mode to allow the entry of fresh air. | 100 | C |  | C
EFB-RS-260 | If the electric power consumption of the HVAC unit is higher than 20kW, the Supplier shall explain during the tender stage the actions considered in the design of the HVAC unit to avoid the fire propagation from the HVAC unit to the passenger area, per Position 9 of the EN45545-3. | EFB-RS-260 | If the electric power consumption of the HVAC unit is higher than 20kW, the Supplier shall explain during the tender stage the actions considered in the design of the HVAC unit to avoid the fire propagation from the HVAC unit to the passenger area, per Position 9 of the EN45545-3. | 100 | C |  | C
EFB-RS-262 | The ventilation shall pressurize the car with all doors and windows closed and car stationary. The proposed value of pressure and the leakage section required to fulfil it shall be submitted during the tender stage. | EFB-RS-262 | The ventilation shall pressurize the car with all doors and windows closed and car stationary. The proposed value of pressure and the leakage section required to fulfil it shall be submitted during the tender stage. | 100 | C |  | C
EFB-RS-263 | Ventilation shall form a positive static pressure of maximum 40Pa in within when the vehicle windows and doors are closed and while the vehicle stops or moves. | EFB-RS-263 | Ventilation shall form a positive static pressure of maximum 40Pa in within when the vehicle windows and doors are closed and while the vehicle stops or moves. | 100 | C | HC_230517: It is necessary to adjust flow rates exhaust and dampers position according to the final requirements in each car during the type factory tests. | C | HC_230517: It is necessary to adjust flow rates exhaust and dampers position according to the final requirements in each car during the type factory tests.
EFB-RS-264 | Positive interior pressure must be maintained at all car speeds regardless of the car’s position in a consist or direction of travel. | EFB-RS-264 | Positive interior pressure must be maintained at all car speeds regardless of the car’s position in a consist or direction of travel. | 100 | C |  | C
EFB-RS-265 | The Supplier will choose the evaporator fan in order to comply with the points defined in Section 3 PERFORMANCES taking into consideration the design of the specific air ducting of this vehicle. | EFB-RS-265 | The Supplier will choose the evaporator fan in order to comply with the points defined in Section 3 PERFORMANCES taking into consideration the design of the specific air ducting of this vehicle. | 100 | C |  | C
EFB-RS-266 | The train unit will be fitted with force air exhausting. Air exhausting will be located inside the HVAC units. | EFB-RS-266 | The train unit will be fitted with force air exhausting. Air exhausting will be located inside the HVAC units. | 100 | C |  | C
EFB-RS-267 | The Supplier will calculate during the tender stage the leakage section required in the train in order to comply with the previous requirement considering the fresh airflow is regulated (fresh air damper). The Supplier will also confirm the value of the static pressure achievable for the proposed fresh airflow in the different cars. | EFB-RS-267 | The Supplier will calculate during the tender stage the leakage section required in the train in order to comply with the previous requirement considering the fresh airflow is regulated (fresh air damper). The Supplier will also confirm the value of the static pressure achievable for the proposed fresh airflow in the different cars. | 100 | C | HC_230517: These values will be verified in Factory type tests. | C | HC_230517: These values will be verified in Factory type tests.
EFB-RS-268 | The HVAC unit (considering exhaust is incluided in the HVAC unit) shall be equipped with pneumatic dampers in the fresh air inlets in order to mitigate the entry of the external pressure waves generated in tunnels into the Unit interior. These dampers will be active closing before entering a tunnel. | EFB-RS-268 | The HVAC unit (considering exhaust is incluided in the HVAC unit) shall be equipped with pneumatic dampers in the fresh air inlets in order to mitigate the entry of the external pressure waves generated in tunnels into the Unit interior. These dampers will be active closing before entering a tunnel. | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-270 | The Supplier will provide as OPTION 6 pneumatic air dampers to be fitted in the supply air duct to the toilets, in order to avoid the overpressure inside the toilets when the exhaust unit is stopped. | EFB-RS-270 | The Supplier will provide as OPTION 6 pneumatic air dampers to be fitted in the supply air duct to the toilets, in order to avoid the overpressure inside the toilets when the exhaust unit is stopped. | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-272 | The Supplier will provide during the tender stage the characteristic curve P-Q of the proposed evaporator motor-fan. | EFB-RS-272 | The Supplier will provide during the tender stage the characteristic curve P-Q of the proposed evaporator motor-fan. | 100 | C |  | C
EFB-RS-273 | The Supplier will provide during the tender stage the characteristic curve P-Q of the proposed exhaust motor-fan. | EFB-RS-273 | The Supplier will provide during the tender stage the characteristic curve P-Q of the proposed exhaust motor-fan. | 100 | C |  | C
EFB-RS-275 | The control of the HVAC system shall automatically operate in order to control the temperature throughout the passenger area, according to the parameters that will be agreed during the project, and will be adjusted by authorized personnel. | EFB-RS-275 | The control of the HVAC system shall automatically operate in order to control the temperature throughout the passenger area, according to the parameters that will be agreed during the project, and will be adjusted by authorized personnel. | 100 | C |  | C
EFB-RS-276 | All the elements to control and protect the HVAC system shall be integrated in the control panel, comprising not only the electronic controller but also the electric panel. | EFB-RS-276 | All the elements to control and protect the HVAC system shall be integrated in the control panel, comprising not only the electronic controller but also the electric panel. | 100 | C |  | C
EFB-RS-278 | For the basic option, the control of the HVAC system shall provide the signals to connect/disconnect the floor heat solution in 2 separated stages as minimum . The Supplier shall collaborate with CAF in the definition of the circuit breakers and contactors for the floor heaters, but these components will be provided by CAF. | EFB-RS-278 | For the basic option, the control of the HVAC system shall provide the signals to connect/disconnect the floor heat solution in 2 separated stages as minimum . The Supplier shall collaborate with CAF in the definition of the circuit breakers and contactors for the floor heaters, but these components will be provided by CAF. | 100 | C |  | C
EFB-RS-279 | Based on the information of the room temperature sensor, the return air temperature sensor and the room temperature setting, the proportional integral (PI) regulation will be adopted to control the floor heaters. | EFB-RS-279 | Based on the information of the room temperature sensor, the return air temperature sensor and the room temperature setting, the proportional integral (PI) regulation will be adopted to control the floor heaters. | 100 | C |  | C
EFB-RS-280 | The Supplier shall confirm how the modulation of the floor heating power shall be made, in order to ensure the temperature uniformity levels requested in the EN14750-1 for a class A vehicle are achieved for any heating load. | EFB-RS-280 | The Supplier shall confirm how the modulation of the floor heating power shall be made, in order to ensure the temperature uniformity levels requested in the EN14750-1 for a class A vehicle are achieved for any heating load. | 100 | C |  | C
EFB-RS-281 | Ventilation and fresh air flow in the passenger deparment shall be mantained in case the electronics is not available. The supplier shall specify how it is achieved. | EFB-RS-281 | Ventilation and fresh air flow in the passenger deparment shall be mantained in case the electronics is not available. The supplier shall specify how it is achieved. | 100 | C |  | C
EFB-RS-282 | All the control elements shall operate from the train DC voltage. Voltage range and characteristics as defined in (EFFAE general) specification. | EFB-RS-282 | All the control elements shall operate from the train DC voltage. Voltage range and characteristics as defined in (EFFAE general) specification. | 100 | C |  | C
EFB-RS-283 | The Supplier shall indicate the total power drawn by the controller and the electric panel. | EFB-RS-283 | The Supplier shall indicate the total power drawn by the controller and the electric panel. | 100 | C |  | C
EFB-RS-284 | The offer shall define the type and quantity of inputs and outputs available in the electronic control unit as well as their main electrical characteristics. | EFB-RS-284 | The offer shall define the type and quantity of inputs and outputs available in the electronic control unit as well as their main electrical characteristics. | 100 | C |  | C
EFB-RS-285 | The Supplier will define during the tender stage the type of contactors used (manufacturer, family, rating…). The contactors shall be service proven in a rail-transit environment. | EFB-RS-285 | The Supplier will define during the tender stage the type of contactors used (manufacturer, family, rating…). The contactors shall be service proven in a rail-transit environment. | 100 | C |  | C
EFB-RS-286 | The HVAC units shall have staggered starting in a sequence to reduce the inrush current load on the auxiliary power supply due to simultaneous starting of air-con motors. This may be achieved through the communication between the electronic controller of the HVAC unit and TCMS. In case of communication fault, the control unit shall implement a logic in order to ensure also this staggered starting. The Supplier shall explain during the tender stage this logic. | EFB-RS-286 | The HVAC units shall have staggered starting in a sequence to reduce the inrush current load on the auxiliary power supply due to simultaneous starting of air-con motors. This may be achieved through the communication between the electronic controller of the HVAC unit and TCMS. In case of communication fault, the control unit shall implement a logic in order to ensure also this staggered starting. The Supplier shall explain during the tender stage this logic. | 100 | C |  | C
EFB-RS-287 | Once power is restored following any loss of power, arising from negotiating neutral sections or otherwise, each HVAC unit shall automatically return to its last operational mode. The HVAC units shall be sequence started in this case as well. | EFB-RS-287 | Once power is restored following any loss of power, arising from negotiating neutral sections or otherwise, each HVAC unit shall automatically return to its last operational mode. The HVAC units shall be sequence started in this case as well. | 100 | C |  | C
EFB-RS-288 | The controller must be fitted with a CAN series communication port via which it is possible to connect to the TCMS for controlling purposes, and an Ethernet port for maintenance and diagnosis purposes. | EFB-RS-288 | The controller must be fitted with a CAN series communication port via which it is possible to connect to the TCMS for controlling purposes, and an Ethernet port for maintenance and diagnosis purposes. | 100 | C |  | C
EFB-RS-289 | The controller will publish on the CAN all the information related to the status of the HVAC system, including the status of all digital and analogical input/outputs wired and also internal faults. | EFB-RS-289 | The controller will publish on the CAN all the information related to the status of the HVAC system, including the status of all digital and analogical input/outputs wired and also internal faults. | 100 | C |  | C
EFB-RS-290 | The specific information to be exchanged by bus with the TCMS will be agreed during design stage. | EFB-RS-290 | The specific information to be exchanged by bus with the TCMS will be agreed during design stage. | 100 | C |  | C
EFB-RS-291 | At least the following faults shall be reported to TCMS. (i) Compressor overload thermal cut-out (ii) Ventilation blower failure (iii) Saloon over-temperature (iv) HP switch activation (vi) LP switch activation | EFB-RS-291 | At least the following faults shall be reported to TCMS. (i) Compressor overload thermal cut-out (ii) Ventilation blower failure (iii) Saloon over-temperature (iv) HP switch activation (vi) LP switch activation | 100 | C |  | C
EFB-RS-292 | The interior temperature will be automatically controlled according to regulation curve proposed in annex A of EN 14750-1:2006 standard for a class A vehicle. | EFB-RS-292 | The interior temperature will be automatically controlled according to regulation curve proposed in annex A of EN 14750-1:2006 standard for a class A vehicle. | 100 | C |  | C
EFB-RS-293 | This regulation curve could be displaced up or down by maintenance staff in a workshop environment, according to a parameter adjustable by software. The limits will be defined during the project. | EFB-RS-293 | This regulation curve could be displaced up or down by maintenance staff in a workshop environment, according to a parameter adjustable by software. The limits will be defined during the project. | 100 | C |  | C
EFB-RS-294 | The HVAC system will be running in ventilation mode when cooling or heating is not required. | EFB-RS-294 | The HVAC system will be running in ventilation mode when cooling or heating is not required. | 100 | C |  | C
EFB-RS-295 | The Supplier shall explain during the tender stage which functionalities are available through CAN and which are available through the Ethernet port. | EFB-RS-295 | The Supplier shall explain during the tender stage which functionalities are available through CAN and which are available through the Ethernet port. | 100 | C |  | C
EFB-RS-296 | In the event of high pressure cut-out being activated by malfunction of the HVAC unit, means shall be provided to inhibit further operation of the compressor and prevent self-reset of the cut-out device. | EFB-RS-296 | In the event of high pressure cut-out being activated by malfunction of the HVAC unit, means shall be provided to inhibit further operation of the compressor and prevent self-reset of the cut-out device. | 100 | C |  | C
EFB-RS-297 | In the event of the high pressure being built up due to temporary abnormal high ambient temperature, the system shall unload without tripping the compressor circuit breaker and permit the high-cut device to be self reset when conditions resume normal. | EFB-RS-297 | In the event of the high pressure being built up due to temporary abnormal high ambient temperature, the system shall unload without tripping the compressor circuit breaker and permit the high-cut device to be self reset when conditions resume normal. | 100 | C |  | C
EFB-RS-298 | In the event that all conditions revert to normal without malfunction in the system, the unloading device shall be reset and the system shall load up automatically. | EFB-RS-298 | In the event that all conditions revert to normal without malfunction in the system, the unloading device shall be reset and the system shall load up automatically. | 100 | C |  | C
EFB-RS-299 | A self-test is performed when the controller is switched on. In this process, the controller tests all temperature sensors, tests the BUS system initialization, etc. Then the controller records the result of the self-test and sends it to the train computer. After self-test process, the controller switches to “off mode” and waits for operation start command. | EFB-RS-299 | A self-test is performed when the controller is switched on. In this process, the controller tests all temperature sensors, tests the BUS system initialization, etc. Then the controller records the result of the self-test and sends it to the train computer. After self-test process, the controller switches to “off mode” and waits for operation start command. | 100 | NC | HC_230517: The HVAC diagnostic is always running. If something more specific is necessary for this requirement, the proposal of autotest could be used. The autotest must be included and is not enough with normal diagnosis during service. Please to define the autotest sequence during design stage. Ok, same autotest sequence than previus project can be used. | NC | HC_230517: The HVAC diagnostic is always running. If something more specific is necessary for this requirement, the proposal of autotest could be used. The autotest must be included and is not enough with normal diagnosis during service. Please to define the autotest sequence during design stage. Ok, same autotest sequence than previus project can be used.
EFB-RS-300 | The system gives the option to monitor the performance and observe events, as well as possible failures in real time and historic through a PC connected to the control, through the Ethernet interface located in the control panel. • Allows monitoring in real time, which means, obtaining wide information on all parameters of the working equipment, for investigation or for verification tests for the user. • Allows observing failures in real time or failures that occurred previously, catching and analysing the memory in order to examine temperatures, states and working hours of the equipment. • Allows activation / deactivation of all outputs. • Allows loading new editions of software of the system. | EFB-RS-300 | The system gives the option to monitor the performance and observe events, as well as possible failures in real time and historic through a PC connected to the control, through the Ethernet interface located in the control panel. • Allows monitoring in real time, which means, obtaining wide information on all parameters of the working equipment, for investigation or for verification tests for the user. • Allows observing failures in real time or failures that occurred previously, catching and analysing the memory in order to examine temperatures, states and working hours of the equipment. • Allows activation / deactivation of all outputs. • Allows loading new editions of software of the system. | 100 | C |  | C
EFB-RS-301 | Temperature adjustment, and working mode can be changed via maintenance software. | EFB-RS-301 | Temperature adjustment, and working mode can be changed via maintenance software. | 100 | C |  | C
EFB-RS-302 | Moreover, the service software shall bring the following capabilities: • Real-time monitoring of application variables, in tabular and customized views. • Modification of variable values, and hence adjust application run-time behaviour. • Upload new applications, kernels, and customized files to the controller. • Ability to view temperature and operational hour statistics over the lifetime of the PLC. • Configuration of Real Time Clock (RTC) and network address settings. • Ability to view version information and resource usage of the running application. • Download of log and statistics files for data generated by the application. | EFB-RS-302 | Moreover, the service software shall bring the following capabilities: • Real-time monitoring of application variables, in tabular and customized views. • Modification of variable values, and hence adjust application run-time behaviour. • Upload new applications, kernels, and customized files to the controller. • Ability to view temperature and operational hour statistics over the lifetime of the PLC. • Configuration of Real Time Clock (RTC) and network address settings. • Ability to view version information and resource usage of the running application. • Download of log and statistics files for data generated by the application. | 100 | NC | HC_230517: The software does not allow custom or configurable views. The same configurations and views proposed in other projects will be available. only the customize of the screens is not complied. The interface can be customized at the beginning of the project, but not during the usual maintenance connection. Same solution to AMYA. | NC | HC_230517: The software does not allow custom or configurable views. The same configurations and views proposed in other projects will be available. only the customize of the screens is not complied. The interface can be customized at the beginning of the project, but not during the usual maintenance connection. Same solution to AMYA.
EFB-RS-303 | The HVAC unit shall provide a "Testing mode". In this mode it shall be possible to force the HVAC system to operate in any cooling, heating and ventilation configuration, regardless of ambient temperature, fresh, return or other monitored condition. | EFB-RS-303 | The HVAC unit shall provide a "Testing mode". In this mode it shall be possible to force the HVAC system to operate in any cooling, heating and ventilation configuration, regardless of ambient temperature, fresh, return or other monitored condition. | 100 | C |  | C
EFB-RS-304 | During these forced functions, no damage shall result to any component or equipment. | EFB-RS-304 | During these forced functions, no damage shall result to any component or equipment. | 100 | NC | HC_230517: This will depend on th skill level of the operator. Safety protections of the unit will be working normally within the forced mode. | NC | HC_230517: This will depend on th skill level of the operator. Safety protections of the unit will be working normally within the forced mode.
EFB-RS-305 | The software required for the diagnostic, downloading registers and setting of the parameters will be provided by the Supplier. The functionalities and the visual interface of this software shall be agreed with the final customer during the project. | EFB-RS-305 | The software required for the diagnostic, downloading registers and setting of the parameters will be provided by the Supplier. The functionalities and the visual interface of this software shall be agreed with the final customer during the project. | 100 | C |  | C
EFB-RS-306 | The replacement of any HVAC electronic control unit shall be recognized by the network without need for manual reconfiguration of addresses and software already installed (plug and play type). | EFB-RS-306 | The replacement of any HVAC electronic control unit shall be recognized by the network without need for manual reconfiguration of addresses and software already installed (plug and play type). | 100 | C |  | C
EFB-RS-307 | The faults will be recorded in the memory of the controller. The capacity of the memory will be big enough as to store all the faults between 2 maintenance operations. The memory could be deleted after the maintenance operation. The Supplier will provide details during the tender stage about the capacity of the memory. | EFB-RS-307 | The faults will be recorded in the memory of the controller. The capacity of the memory will be big enough as to store all the faults between 2 maintenance operations. The memory could be deleted after the maintenance operation. The Supplier will provide details during the tender stage about the capacity of the memory. | 100 | C |  | C
EFB-RS-308 | Together with each recorded fault following information will be recorded: - Severity of fault - State - Date - Time | EFB-RS-308 | Together with each recorded fault following information will be recorded: - Severity of fault - State - Date - Time | 100 | C |  | C
EFB-RS-309 | All the electronic control boards will be protected with a varnish according to an acceptable protection procedure. | EFB-RS-309 | All the electronic control boards will be protected with a varnish according to an acceptable protection procedure. | 100 | C |  | C
EFB-RS-311 | The refrigerant piping shall be of copper with suitable non-ferrous fittings. The connections between the piping and equipment shall be made using brazed joints. | EFB-RS-311 | The refrigerant piping shall be of copper with suitable non-ferrous fittings. The connections between the piping and equipment shall be made using brazed joints. | 100 | C |  | C
EFB-RS-312 | There may be relative movement between the terminals of the compressor, condenser and evaporator coils resulting from vibration. The pipe layout shall take this aspect into consideration. | EFB-RS-312 | There may be relative movement between the terminals of the compressor, condenser and evaporator coils resulting from vibration. The pipe layout shall take this aspect into consideration. | 100 | C |  | C
EFB-RS-313 | The vibration eliminators in the compressor connections will be service proven and will provide a high reliability. | EFB-RS-313 | The vibration eliminators in the compressor connections will be service proven and will provide a high reliability. | 100 | C |  | C
EFB-RS-314 | The Supplied will confirm during the tender stage the number and location of screw couplings in the proposed cooling circuit. This number will be reduced down to the minimum. | EFB-RS-314 | The Supplied will confirm during the tender stage the number and location of screw couplings in the proposed cooling circuit. This number will be reduced down to the minimum. | 100 | C |  | C
EFB-RS-315 | The Supplier will confirm during the tender stage the leakage rate per year of the proposed HVAC unit. This value will be contractual. The leakage rate per screw coupling will be lower than 3g/year. | EFB-RS-315 | The Supplier will confirm during the tender stage the leakage rate per year of the proposed HVAC unit. This value will be contractual. The leakage rate per screw coupling will be lower than 3g/year. | 100 | NC | HC_230517: Up to 100 gr / year / unit, agreed value for all previous projects. The therocal calculation is12 unit of screw connection per refrigerant circuit. Pressure switches (4) , transducers(4), lloading valves (4). 5 g/year/screw connection. Total 60g/year. | NC | HC_230517: Up to 100 gr / year / unit, agreed value for all previous projects. The therocal calculation is12 unit of screw connection per refrigerant circuit. Pressure switches (4) , transducers(4), lloading valves (4). 5 g/year/screw connection. Total 60g/year.
EFB-RS-316 | The leakage rate of the proposed cooling circuit will be lower enough as to ensure it is not necessary to refill the cooling circuit between major overhauls (10 years). | EFB-RS-316 | The leakage rate of the proposed cooling circuit will be lower enough as to ensure it is not necessary to refill the cooling circuit between major overhauls (10 years). | 100 | C |  | C
EFB-RS-317 | Screw couplings will be permitted only where necessary for disconnecting the refrigerant circuit for maintenance. Automatic shut off facilities shall be provided with the couplings to prevent loss of refrigerant for the disconnection. All other connections shall be of a permanent type. | EFB-RS-317 | Screw couplings will be permitted only where necessary for disconnecting the refrigerant circuit for maintenance. Automatic shut off facilities shall be provided with the couplings to prevent loss of refrigerant for the disconnection. All other connections shall be of a permanent type. | 100 | C | HC_230517: Schrader valves are considered. 12 unit per refrigerant circuit. Pressure switches, transducers, lloading valves. | C | HC_230517: Schrader valves are considered. 12 unit per refrigerant circuit. Pressure switches, transducers, lloading valves.
EFB-RS-318 | The refrigeration piping system shall be effectively dehydrated prior to charging. The HVAC equipment manufacturer shall evacuate and dehydrate the system to less than 125 microns. | EFB-RS-318 | The refrigeration piping system shall be effectively dehydrated prior to charging. The HVAC equipment manufacturer shall evacuate and dehydrate the system to less than 125 microns. | 100 | NC | HC_230517: According to the internal HC procedure used for all previous projects, this value reaches -1 to -0.91 bar (manometric reference). HC Procedure “ITT-006-10 Tightness, vacuum and refrigerant charge tests in HVAC.procedure”. Taking 125 microns as an absolute pressure reference, this equates to 0.00016 bar (absolute pressure reference), too much for standard procedures and special tools would be required to achieve this if necessary. | NC | HC_230517: According to the internal HC procedure used for all previous projects, this value reaches -1 to -0.91 bar (manometric reference). HC Procedure “ITT-006-10 Tightness, vacuum and refrigerant charge tests in HVAC.procedure”. Taking 125 microns as an absolute pressure reference, this equates to 0.00016 bar (absolute pressure reference), too much for standard procedures and special tools would be required to achieve this if necessary.
EFB-RS-319 | A replaceable and maintainable filter/ dryer shall be installed in the refrigerant circuit. The dehydration device shall have sufficient capacity to absorb any moisture entering the system during operation. The dehydrator shall not require servicing between overhauls. | EFB-RS-319 | A replaceable and maintainable filter/ dryer shall be installed in the refrigerant circuit. The dehydration device shall have sufficient capacity to absorb any moisture entering the system during operation. The dehydrator shall not require servicing between overhauls. | 100 | C |  | C
EFB-RS-320 | Means shall be provided to avoid loss of refrigerant to atmosphere during charging and extraction. | EFB-RS-320 | Means shall be provided to avoid loss of refrigerant to atmosphere during charging and extraction. | 100 | C |  | C
EFB-RS-321 | The offer shall indicate the schematic of the cooling circuit . | EFB-RS-321 | The offer shall indicate the schematic of the cooling circuit . | 100 | C |  | C
EFB-RS-322 | The Supplier will confirm during the tender stage if it is necessary to install a hot gas bypass in the cooling circuit in order to reach the required uniformity in EN14750-1 standard for a category A vehicle, having into account the foreseen air ducts and the cooling power required for this application. | EFB-RS-322 | The Supplier will confirm during the tender stage if it is necessary to install a hot gas bypass in the cooling circuit in order to reach the required uniformity in EN14750-1 standard for a category A vehicle, having into account the foreseen air ducts and the cooling power required for this application. | 100 | C | HC_230517: the initial proposal, is provide a bypass valve in the circuit, and only for cooling mode. | C | HC_230517: the initial proposal, is provide a bypass valve in the circuit, and only for cooling mode.
EFB-RS-323 | The refrigerant system and components shall meet all pressure safety design requirements of EN 378. | EFB-RS-323 | The refrigerant system and components shall meet all pressure safety design requirements of EN 378. | 100 | C |  | C
EFB-RS-324 | A label displaying the refrigerant type employed shall be: (a) permanently affixed in close proximity to the refrigerant charging points; and (b) clearly visible. | EFB-RS-324 | A label displaying the refrigerant type employed shall be: (a) permanently affixed in close proximity to the refrigerant charging points; and (b) clearly visible. | 100 | C |  | C
EFB-RS-325 | The cooling circuit will not be fitted with a refrigerant reservoir. | EFB-RS-325 | The cooling circuit will not be fitted with a refrigerant reservoir. | 100 | NC | HC_230517: A refrigerant reservoir is neccesary for Heat pump mode. | NC | HC_230517: A refrigerant reservoir is neccesary for Heat pump mode.
EFB-RS-326 | The thermal expansion valves shall be accessible via the maintenance cover from the roof. | EFB-RS-326 | The thermal expansion valves shall be accessible via the maintenance cover from the roof. | 100 | C |  | C
EFB-RS-327 | Charging valves for drain and filling refrigerant are available from outside the unit. The Supplier shall send a proposal for the type of charging valve, but the final type must be approved by the final Customer. | EFB-RS-327 | Charging valves for drain and filling refrigerant are available from outside the unit. The Supplier shall send a proposal for the type of charging valve, but the final type must be approved by the final Customer. | 100 | C | HC_230517: The charging valves are located inside the HVAC, easily accessible on the side of the condenser under its cover. The standard valves used in all projects have been considered. In case the end customer requires special valves, these should be offered separately. | C | HC_230517: The charging valves are located inside the HVAC, easily accessible on the side of the condenser under its cover. The standard valves used in all projects have been considered. In case the end customer requires special valves, these should be offered separately.
EFB-RS-328 | Brazing procedure for copper pipes is qualified according to UNE-EN-13134. | EFB-RS-328 | Brazing procedure for copper pipes is qualified according to UNE-EN-13134. | 100 | C |  | C
EFB-RS-329 | The Supplier shall submit during the design stage the 3D model of the cooling circuit pipework for further validation. The aim is to prevent sharp / closed bends, small diameter pipes and long stretches without fastening (breakages due to vibrations), excessive number of joints, etc. | EFB-RS-329 | The Supplier shall submit during the design stage the 3D model of the cooling circuit pipework for further validation. The aim is to prevent sharp / closed bends, small diameter pipes and long stretches without fastening (breakages due to vibrations), excessive number of joints, etc. | 100 | C |  | C
EFB-RS-331 | The Supplier shall collaborate with CAF in the design of the ducts in order to have a correct air distribution and shall approve the ducting design. The Supplier will provide before milestone 1 the next information as for the evaporator motor fan, as for the exhaust fan: -The speed profile (value and direction) at the air supply connection. -The P-Q curve of the motor fan -The internal pressure drop of the HVAC equipment (especified for each component). The Supplier shall collaborate with CAF in the follow-up of the global pressure drops (supply and return ducts, HVAC equipment & saloon overpressure) so that compatibility of the evaporator motor-fan is ensured after final adjustments. In case CFD simulations for air ducts and thermal comfort are performed by CAF, the Supplier will provide CAF with support for these simulations, and will validate the results. | EFB-RS-331 | The Supplier shall collaborate with CAF in the design of the ducts in order to have a correct air distribution and shall approve the ducting design. The Supplier will provide before milestone 1 the next information as for the evaporator motor fan, as for the exhaust fan: -The speed profile (value and direction) at the air supply connection. -The P-Q curve of the motor fan -The internal pressure drop of the HVAC equipment (especified for each component). The Supplier shall collaborate with CAF in the follow-up of the global pressure drops (supply and return ducts, HVAC equipment & saloon overpressure) so that compatibility of the evaporator motor-fan is ensured after final adjustments. In case CFD simulations for air ducts and thermal comfort are performed by CAF, the Supplier will provide CAF with support for these simulations, and will validate the results. | 100 | C | HC_230517: Some of the parameters needs to be measured in a mock up or type test and it is not possible in milestone 1, so, HC will provide for tender stage the Pressure drop definition sheet completed. In mock up the confirmation of these values. | C | HC_230517: Some of the parameters needs to be measured in a mock up or type test and it is not possible in milestone 1, so, HC will provide for tender stage the Pressure drop definition sheet completed. In mock up the confirmation of these values.
EFB-RS-332 | The ducts shall be fully lagged with non-combustible insulation material to prevent the formation of condensation. | EFB-RS-332 | The ducts shall be fully lagged with non-combustible insulation material to prevent the formation of condensation. | 100 | NA |  | NA
EFB-RS-333 | The Supplier of the HVAC equipment will recommend about the minimum insulating value to use for insulation of the air ducts. | EFB-RS-333 | The Supplier of the HVAC equipment will recommend about the minimum insulating value to use for insulation of the air ducts. | 100 | C |  | C
EFB-RS-334 | The Supplier of the HVAC equipment will recommend about the most suitable location for the recirculated air grilles. | EFB-RS-334 | The Supplier of the HVAC equipment will recommend about the most suitable location for the recirculated air grilles. | 100 | C |  | C
EFB-RS-335 | Air velocity within the vehicle shall be in the limits in Annex-B of EN 14750-1 for the comfort region. | EFB-RS-335 | Air velocity within the vehicle shall be in the limits in Annex-B of EN 14750-1 for the comfort region. | 100 | C |  | C
EFB-RS-336 | The Supplier will inform during the tender stage about the maximum temperature uniformity that can be achieved as in cooling as in heating mode, having into account the length of the HVAC equipment and the lack of air distribution ducting below the condenser area. | EFB-RS-336 | The Supplier will inform during the tender stage about the maximum temperature uniformity that can be achieved as in cooling as in heating mode, having into account the length of the HVAC equipment and the lack of air distribution ducting below the condenser area. | 100 | C | HC_230517: 4 k According to EN 14750 A Category | C | HC_230517: 4 k According to EN 14750 A Category
EFB-RS-338 | The fresh air intakes of the HVAC system shall be equipped with grilles the design of which shall be such that it prevents ingress of snow, frost, water and heavier impurities to the filter and into the ventilation system. Special consideration will be taken to the characteristic metal dust usual of this application. | EFB-RS-338 | The fresh air intakes of the HVAC system shall be equipped with grilles the design of which shall be such that it prevents ingress of snow, frost, water and heavier impurities to the filter and into the ventilation system. Special consideration will be taken to the characteristic metal dust usual of this application. | 100 | C |  | C
EFB-RS-339 | The grilles will include water eliminating baffles or louvers that shall be designed to prevent snow and water ingress resulting from adverse weather or train washing. | EFB-RS-339 | The grilles will include water eliminating baffles or louvers that shall be designed to prevent snow and water ingress resulting from adverse weather or train washing. | 100 | C |  | C
EFB-RS-341 | The air flow through the grilles will not be faster than 2 m/s. The Supplier shall define during the tender stage the air speed considered in the design of the air intakes. | EFB-RS-341 | The air flow through the grilles will not be faster than 2 m/s. The Supplier shall define during the tender stage the air speed considered in the design of the air intakes. | 100 | C |  | C
EFB-RS-344 | Folded air filters will be provided in order to increase the filtering surface. | EFB-RS-344 | Folded air filters will be provided in order to increase the filtering surface. | 100 | C |  | C
EFB-RS-345 | The Supplier will confirm during the tender stage the total dust holding capacity of the proposed filter (g). | EFB-RS-345 | The Supplier will confirm during the tender stage the total dust holding capacity of the proposed filter (g). | 100 | C |  | C
EFB-RS-346 | Filters will consist on a filtering element fixed to a frame. Only the filtering element should be changed as a maintenance operation. | EFB-RS-346 | Filters will consist on a filtering element fixed to a frame. Only the filtering element should be changed as a maintenance operation. | 100 | NC | HC_230517: Cartridge filters considered in the initial offer | NC | HC_230517: Cartridge filters considered in the initial offer
EFB-RS-347 | Air filters shall be located in such a manner that it (they) shall be easily replaced/installed via a maintenance cover. | EFB-RS-347 | Air filters shall be located in such a manner that it (they) shall be easily replaced/installed via a maintenance cover. | 100 | C | HC_230517: Via external maintenence cover in the roof | C | HC_230517: Via external maintenence cover in the roof
EFB-RS-348 | Ensure that accessibility to the filter either by quick fasteners or by using the fewer screws possibly. Avoid also the use of flat screws, preferibely hexagonal screws. | EFB-RS-348 | Ensure that accessibility to the filter either by quick fasteners or by using the fewer screws possibly. Avoid also the use of flat screws, preferibely hexagonal screws. | 100 | C |  | C
EFB-RS-349 | Maintenance personnel shall have full, unconstrained access allowing use of both hands to remove and replace air filters without the need to remove and/or move any additional component. | EFB-RS-349 | Maintenance personnel shall have full, unconstrained access allowing use of both hands to remove and replace air filters without the need to remove and/or move any additional component. | 100 | C |  | C
EFB-RS-350 | Air speed in the filters shall not exceed 2,4 m/s as an average and in no point the value 4 m/s. | EFB-RS-350 | Air speed in the filters shall not exceed 2,4 m/s as an average and in no point the value 4 m/s. | 100 | C |  | C
EFB-RS-351 | The filters and filter holders shall be sealed at their edges to prevent filter by-pass. | EFB-RS-351 | The filters and filter holders shall be sealed at their edges to prevent filter by-pass. | 100 | C |  | C
EFB-RS-352 | Support of the filter elements shall be provided to prevent blowout of the filter elements under clogged filter conditions. | EFB-RS-352 | Support of the filter elements shall be provided to prevent blowout of the filter elements under clogged filter conditions. | 100 | C |  | C
EFB-RS-353 | Filters shall have airflow directional arrows on the filter frame. | EFB-RS-353 | Filters shall have airflow directional arrows on the filter frame. | 100 | C |  | C
EFB-RS-354 | The air filters shall not become wet under any circumstances. | EFB-RS-354 | The air filters shall not become wet under any circumstances. | 100 | C |  | C
EFB-RS-355 | The Supplier will confirm the value of the pressure drop to consider in the filter when clean and when dirty. | EFB-RS-355 | The Supplier will confirm the value of the pressure drop to consider in the filter when clean and when dirty. | 100 | C |  | C
EFB-RS-356 | Maximum filter air face velocity shall not exceed the manufacturer’s recommendation even at the end of the scheduled maintenance interval . | EFB-RS-356 | Maximum filter air face velocity shall not exceed the manufacturer’s recommendation even at the end of the scheduled maintenance interval . | 100 | C |  | C
EFB-RS-358 | Each HVAC unit will be provided with evaporator section. | EFB-RS-358 | Each HVAC unit will be provided with evaporator section. | 100 | C |  | C
EFB-RS-360 | The evaporator section unit shall be of adequate capacity to filter, cool, dehumidify and control the temperature of the air without condensate carry over or unacceptable noise level. | EFB-RS-360 | The evaporator section unit shall be of adequate capacity to filter, cool, dehumidify and control the temperature of the air without condensate carry over or unacceptable noise level. | 100 | C |  | C
EFB-RS-361 | Each blower and motor assembly shall blow the air from the mixing plenum through the evaporator and force it into the supply-air ducts from where it shall be discharge into the passenger areas. The motor and blower wheel assembly shall be dynamically balanced. The blower wheel and volute design shall ensure that, the airflow is stable so that the noise requirements can be achieved. | EFB-RS-361 | Each blower and motor assembly shall blow the air from the mixing plenum through the evaporator and force it into the supply-air ducts from where it shall be discharge into the passenger areas. The motor and blower wheel assembly shall be dynamically balanced. The blower wheel and volute design shall ensure that, the airflow is stable so that the noise requirements can be achieved. | 100 | C |  | C
EFB-RS-363 | The Supplier shall provide a condensate drain beneath the evaporator coil. Baffles shall be provided in the pan to prevent spillage. Suitable means shall be incorporate for cleaning of drainage system. | EFB-RS-363 | The Supplier shall provide a condensate drain beneath the evaporator coil. Baffles shall be provided in the pan to prevent spillage. Suitable means shall be incorporate for cleaning of drainage system. | 100 | C |  | C
EFB-RS-364 | The Supplier shall confirm during the tender stage following characteristics for the evaporator coils: - Material of the fins: Aluminium - Coating of the fins - Fin thickness - Fin pitch - Flat fins or curved - Material of the frame - Bypass factor - Diameter of the Cupper tubes - Configuration of the Cupper tubes - Material of the end plate | EFB-RS-364 | The Supplier shall confirm during the tender stage following characteristics for the evaporator coils: - Material of the fins: Aluminium - Coating of the fins - Fin thickness - Fin pitch - Flat fins or curved - Material of the frame - Bypass factor - Diameter of the Cupper tubes - Configuration of the Cupper tubes - Material of the end plate | 100 | C | HC_230517: These characteristics are defined in the Technical Description | C | HC_230517: These characteristics are defined in the Technical Description
EFB-RS-365 | The coil face area of the evaporator unit shall be sufficiently large to prevent condensate carryover into the fan plenum or main air duct, and to meet the requirements of the condensate carryover test. | EFB-RS-365 | The coil face area of the evaporator unit shall be sufficiently large to prevent condensate carryover into the fan plenum or main air duct, and to meet the requirements of the condensate carryover test. | 100 | C |  | C
EFB-RS-366 | The HVAC system will be fitted with thermal expansion valves, to be installed in the liquid line between condenser and evaporator unit, in order to control the refrigerant flow and to ensure proper evaporating and condensing pressures. Solder connection shall be provided | EFB-RS-366 | The HVAC system will be fitted with thermal expansion valves, to be installed in the liquid line between condenser and evaporator unit, in order to control the refrigerant flow and to ensure proper evaporating and condensing pressures. Solder connection shall be provided | 100 | C |  | C
EFB-RS-367 | Low Pressure and High Pressure protection shall be proposed. The supplier shall indicate the type of protection to be applied. | EFB-RS-367 | Low Pressure and High Pressure protection shall be proposed. The supplier shall indicate the type of protection to be applied. | 100 | C | HC_230517: Pressure switch are provided | C | HC_230517: Pressure switch are provided
EFB-RS-368 | The Supplier will confirm during the tender stage if pressure test ports are provided, to connect and external gauge. The Supplier will send a proposal for the type of test port, but the final type of test-port must be approved by the final Customer. | EFB-RS-368 | The Supplier will confirm during the tender stage if pressure test ports are provided, to connect and external gauge. The Supplier will send a proposal for the type of test port, but the final type of test-port must be approved by the final Customer. | 100 | C |  | C
EFB-RS-369 | The pressure values measured by the pressure transducers shall be available in the communication bus. | EFB-RS-369 | The pressure values measured by the pressure transducers shall be available in the communication bus. | 100 | C |  | C
EFB-RS-370 | The Equipment shall operate at appropriate cooling pressures whereby pre-safety and safety pressures are not reached under the assumption of maximum air temperature is reached. | EFB-RS-370 | The Equipment shall operate at appropriate cooling pressures whereby pre-safety and safety pressures are not reached under the assumption of maximum air temperature is reached. | 100 | C |  | C
EFB-RS-371 | The plenums in the HVAC system shall be insulated to prevent forming condensation. | EFB-RS-371 | The plenums in the HVAC system shall be insulated to prevent forming condensation. | 100 | C |  | C
EFB-RS-374 | The Supplier shall propose the overheating and overloading protection arrangement for the compressor motors. The compressor shall not suffer from any damage due to restarting after previously having shut down without a carry out pumping down cycle. | EFB-RS-374 | The Supplier shall propose the overheating and overloading protection arrangement for the compressor motors. The compressor shall not suffer from any damage due to restarting after previously having shut down without a carry out pumping down cycle. | 100 | C |  | C
EFB-RS-375 | The compressor shall be directly driven and coupled by an ac induction motor and rated for continuous duty at the design capacity. Motor overload protection shall be provided by a thermal cut-out embedded in the windings. | EFB-RS-375 | The compressor shall be directly driven and coupled by an ac induction motor and rated for continuous duty at the design capacity. Motor overload protection shall be provided by a thermal cut-out embedded in the windings. | 100 | C |  | C
EFB-RS-376 | The condenser coil shall consist of Cupper tubes with aluminium fins mechanically crimped to the tubes. | EFB-RS-376 | The condenser coil shall consist of Cupper tubes with aluminium fins mechanically crimped to the tubes. | 100 | C |  | C
EFB-RS-377 | The condenser fan(s) shall provide for adequate airflow over the coil(s) at the design condition. Each fan(s) shall be direct driven by an AC induction motor (3ph) rated for continuous duty. | EFB-RS-377 | The condenser fan(s) shall provide for adequate airflow over the coil(s) at the design condition. Each fan(s) shall be direct driven by an AC induction motor (3ph) rated for continuous duty. | 100 | C |  | C
EFB-RS-379 | The condenser coil shall be located so that it can be cleaned using water from the outside by removing the external covers only. | EFB-RS-379 | The condenser coil shall be located so that it can be cleaned using water from the outside by removing the external covers only. | 100 | C |  | C
EFB-RS-380 | The Supplier will confirm during the tender stage which is the direction of the cooling airflow, to avoid bypassing the hot air to the condenser air inlet and to the evaporator air inlet. The Supplier will consider also for this decision the available distance from the HVAC unit to the roof of the tunnel, to be checked in the drawings provided by CAF. | EFB-RS-380 | The Supplier will confirm during the tender stage which is the direction of the cooling airflow, to avoid bypassing the hot air to the condenser air inlet and to the evaporator air inlet. The Supplier will consider also for this decision the available distance from the HVAC unit to the roof of the tunnel, to be checked in the drawings provided by CAF. | 100 | C |  | C
EFB-RS-381 | The compressor motor shall be protected from overheating due to: (i) Two phase operation. (ii) Low ac supply voltage. (iii) Overload | EFB-RS-381 | The compressor motor shall be protected from overheating due to: (i) Two phase operation. (ii) Low ac supply voltage. (iii) Overload | 100 | C |  | C
EFB-RS-382 | The compressors shall operate from AC power. Voltage range and characteristics as defined in General Specification | EFB-RS-382 | The compressors shall operate from AC power. Voltage range and characteristics as defined in General Specification | 100 | C |  | C
EFB-RS-384 | Fan and motor shall be directly coupled and rated for continuous duty. | EFB-RS-384 | Fan and motor shall be directly coupled and rated for continuous duty. | 100 | C |  | C
EFB-RS-385 | No greasing shall be required for any part of the motor and fan coupling. | EFB-RS-385 | No greasing shall be required for any part of the motor and fan coupling. | 100 | C | HC_230517:Free-Maintenance fans are proposed | C | HC_230517:Free-Maintenance fans are proposed
EFB-RS-386 | Each fan and motor assembly shall be dynamically balanced and constructed from stainless steel or material successfully proven for comparable applications and approved by CAF. The assembly shall be tested to ISO 5801 or comparable national or international standards. | EFB-RS-386 | Each fan and motor assembly shall be dynamically balanced and constructed from stainless steel or material successfully proven for comparable applications and approved by CAF. The assembly shall be tested to ISO 5801 or comparable national or international standards. | 100 | C |  | C
EFB-RS-387 | Condenser motor-fans will be single speed, rated for inverter duty. | EFB-RS-387 | Condenser motor-fans will be single speed, rated for inverter duty. | 100 | C |  | C
EFB-RS-388 | Electrical motors must be brushless type. | EFB-RS-388 | Electrical motors must be brushless type. | 100 | C |  | C
EFB-RS-391 | Overhead heaters shall be integrated inside the HVAC frame. | EFB-RS-391 | Overhead heaters shall be integrated inside the HVAC frame. | 100 | C |  | C
EFB-RS-393 | The 2 stages of overhead heat shall be energized through electro-mechanical contactors capable of modulating the power continuously from zero to full rated power. | EFB-RS-393 | The 2 stages of overhead heat shall be energized through electro-mechanical contactors capable of modulating the power continuously from zero to full rated power. | 100 | NC | HC_230517: conventional contactor are proposed, not solid state contactor (continuous power modulation by one PWM cycle is possible by a solid state contactor, not a conventional one. In any case, the proposed solution is the same as AMYA and all previous HC project) | NC | HC_230517: conventional contactor are proposed, not solid state contactor (continuous power modulation by one PWM cycle is possible by a solid state contactor, not a conventional one. In any case, the proposed solution is the same as AMYA and all previous HC project)
EFB-RS-394 | Modulation shall be effected by a low-frequency PWM cycle controlling the ratio of "heater on" to "heater off" time. | EFB-RS-394 | Modulation shall be effected by a low-frequency PWM cycle controlling the ratio of "heater on" to "heater off" time. | 100 | NC | HC_230517: conventional contactor are proposed, not solid state contactor (continuous power modulation by one PWM cycle is possible by a solid state contactor, not a conventional one. In any case, the proposed solution is the same as AMYA and all previous HC project) | NC | HC_230517: conventional contactor are proposed, not solid state contactor (continuous power modulation by one PWM cycle is possible by a solid state contactor, not a conventional one. In any case, the proposed solution is the same as AMYA and all previous HC project)
EFB-RS-395 | The overhead heating protection concept shall consists of 3 protection level. These safety functions shall be done by means of hardware signals. | EFB-RS-395 | The overhead heating protection concept shall consists of 3 protection level. These safety functions shall be done by means of hardware signals. | 100 | C |  | C
EFB-RS-396 | First Safety Level: The control logic shall ensure that power may not be applied to the overhead heaters unless operation of the blowers is proven. The Supplier will confirm during the tender stage how this target is achieved (current measurements, airflow detection…). | EFB-RS-396 | First Safety Level: The control logic shall ensure that power may not be applied to the overhead heaters unless operation of the blowers is proven. The Supplier will confirm during the tender stage how this target is achieved (current measurements, airflow detection…). | 100 | C |  | C
EFB-RS-397 | Second Safety Level: In addition, the following protection shall be provided at each unit against possible over-temperature conditions: · A primary protection self-resetting thermostat shall be installed adjacent to each overhead heater unit to detect the presence of excessive temperature. | EFB-RS-397 | Second Safety Level: In addition, the following protection shall be provided at each unit against possible over-temperature conditions: · A primary protection self-resetting thermostat shall be installed adjacent to each overhead heater unit to detect the presence of excessive temperature. | 100 | C |  | C
EFB-RS-398 | Upon detection, it shall open the overhead heat contactors supplying that unit; and also the HVAC control receives this failure signal to act accordingly. | EFB-RS-398 | Upon detection, it shall open the overhead heat contactors supplying that unit; and also the HVAC control receives this failure signal to act accordingly. | 100 | C |  | C
EFB-RS-399 | Third Safety Level: A back-up secondary protection thermostat, set at a higher temperature than the primary protection thermostat, shall be provided, to activate a shunt trip type circuit breaker to remove power in the event of a failure of the primary protection thermostat. This protection has to be manually resetted. | EFB-RS-399 | Third Safety Level: A back-up secondary protection thermostat, set at a higher temperature than the primary protection thermostat, shall be provided, to activate a shunt trip type circuit breaker to remove power in the event of a failure of the primary protection thermostat. This protection has to be manually resetted. | 100 | C |  | C
EFB-RS-400 | The trip temperature of the secondary protection thermostat shall be high enough to allow the thermostat to trip only in the event of a failure of the primary protective apparatus (self-resetting thermostat), but still prevent damage to the equipment and other car body components. | EFB-RS-400 | The trip temperature of the secondary protection thermostat shall be high enough to allow the thermostat to trip only in the event of a failure of the primary protective apparatus (self-resetting thermostat), but still prevent damage to the equipment and other car body components. | 100 | C |  | C
EFB-RS-401 | All these Safety level elements shall be duplicated in order to achieve the redundancy required. (i.e. There shall be 2 second safety level thermostats. Both shall detect overtemperature to stop heating). | EFB-RS-401 | All these Safety level elements shall be duplicated in order to achieve the redundancy required. (i.e. There shall be 2 second safety level thermostats. Both shall detect overtemperature to stop heating). | 100 | C |  | C
EFB-RS-402 | The Supplier will propose during the tender stage the tripping temperature of the primary and secondary protection thermostats, and the tolerance of those thermostats. | EFB-RS-402 | The Supplier will propose during the tender stage the tripping temperature of the primary and secondary protection thermostats, and the tolerance of those thermostats. | 100 | C | HC_230517: in this phase some values will be proposed that will be confirmed in the origin type tests | C | HC_230517: in this phase some values will be proposed that will be confirmed in the origin type tests
EFB-RS-403 | The location of the thermostat will be optimized during the type test, but the type of fixation shall ensure its position is not inadvertently changed during preventive maintenance work. Therefore, screwed fastening on slots are forbidden. | EFB-RS-403 | The location of the thermostat will be optimized during the type test, but the type of fixation shall ensure its position is not inadvertently changed during preventive maintenance work. Therefore, screwed fastening on slots are forbidden. | 100 | C |  | C
EFB-RS-404 | The Supplier will confirm during the tender stage if it necessary any thermostat in the Saloon to control the connection/disconnection of the floor heating solution. In case they are needed they will be included inside the scope of supply. | EFB-RS-404 | The Supplier will confirm during the tender stage if it necessary any thermostat in the Saloon to control the connection/disconnection of the floor heating solution. In case they are needed they will be included inside the scope of supply. | 100 | C | HC_230517: the convectors also include two safety thermostats, but not regulation ones | C | HC_230517: the convectors also include two safety thermostats, but not regulation ones
EFB-RS-405 | The floor heating shall be provided via floor heat convectors (OPTION 2). The power shall be divided in 2 stages as minimum. The Supplier shall propose during the tender stage the power per stage. | EFB-RS-405 | The floor heating shall be provided via floor heat convectors (OPTION 2). The power shall be divided in 2 stages as minimum. The Supplier shall propose during the tender stage the power per stage. | 100 | C |  | C
EFB-RS-406 | The Supplier shall define during the tender stage following information for each heat convector: - Heating Power - Airflow - Maximum total pressure drop for the fan - Internal pressure drop of the heat convector | EFB-RS-406 | The Supplier shall define during the tender stage following information for each heat convector: - Heating Power - Airflow - Maximum total pressure drop for the fan - Internal pressure drop of the heat convector | 100 | C |  | C
EFB-RS-407 | The surface temperature of the lining of the heat convectors shall not exceed 60ºC. | EFB-RS-407 | The surface temperature of the lining of the heat convectors shall not exceed 60ºC. | 100 | C |  | C
EFB-RS-408 | The air supplied on the heat convectors shall not exceed 45ºC. | EFB-RS-408 | The air supplied on the heat convectors shall not exceed 45ºC. | 100 | C | HC_230517: C for 45ºC calculated as average value in saloon convector | C | HC_230517: C for 45ºC calculated as average value in saloon convector
EFB-RS-409 | The floor heating solution shall be powered from the auxiliary power unit, at 400VAC 50Hz 3 phase; Voltage range and characteristics as defined in General Specification | EFB-RS-409 | The floor heating solution shall be powered from the auxiliary power unit, at 400VAC 50Hz 3 phase; Voltage range and characteristics as defined in General Specification | 100 | C |  | C
EFB-RS-410 | Each heat convector shall be equipped with a high limit thermostat and back-up protection device. | EFB-RS-410 | Each heat convector shall be equipped with a high limit thermostat and back-up protection device. | 100 | C |  | C
EFB-RS-411 | The location of the protective thermostat will be optimized during the type test, but the final installation of the thermostat shall not enable any displacement from this optimized location. | EFB-RS-411 | The location of the protective thermostat will be optimized during the type test, but the final installation of the thermostat shall not enable any displacement from this optimized location. | 100 | C |  | C
EFB-RS-412 | The maximum dimensions for the heat convectors will be provided by CAF. | EFB-RS-412 | The maximum dimensions for the heat convectors will be provided by CAF. | 100 | C |  | C
EFB-RS-413 | Solutions for overheat and floor heat protection will be designed as a separate function. Under no circumstances will this solution become a part of the function of normal temperature regulation. | EFB-RS-413 | Solutions for overheat and floor heat protection will be designed as a separate function. Under no circumstances will this solution become a part of the function of normal temperature regulation. | 100 | C |  | C
EFB-RS-414 | The control of the overhead heaters and the floor heating solution will be based on software not based on thermostats. Just protections will be based on hardware (thermostats) | EFB-RS-414 | The control of the overhead heaters and the floor heating solution will be based on software not based on thermostats. Just protections will be based on hardware (thermostats) | 100 | C |  | C
EFB-RS-416 | The Supplier will define during the tender stage which are the values considered as to dimension the draining solution in the specific design for this project: 1- Maximum Condensing water flow in the evaporator area in the most severe condition -> X (l/min) 2- Maximum water flow in the condenser area because of rain, washing machines, etc. -> Z (l/min) 3- Maximum water flow in the fresh air inlet area because of rain, washing machines, etc. -> Y (l/min) | EFB-RS-416 | The Supplier will define during the tender stage which are the values considered as to dimension the draining solution in the specific design for this project: 1- Maximum Condensing water flow in the evaporator area in the most severe condition -> X (l/min) 2- Maximum water flow in the condenser area because of rain, washing machines, etc. -> Z (l/min) 3- Maximum water flow in the fresh air inlet area because of rain, washing machines, etc. -> Y (l/min) | 100 | C | HC_230517: 1. 4 l / h. 2. and 3. according to the document" "Clarifications to the W Standards" where all the rain tests are described. | C | HC_230517: 1. 4 l / h. 2. and 3. according to the document" "Clarifications to the W Standards" where all the rain tests are described.
EFB-RS-417 | The draining points in the evaporator area will be designed in order to correctly drain at least 1.5 times X, all along the life of the train. | EFB-RS-417 | The draining points in the evaporator area will be designed in order to correctly drain at least 1.5 times X, all along the life of the train. | 100 | C |  | C
EFB-RS-418 | The draining points in the condenser area will be designed in order to correctly drain at least 1.5 times Z, all along the life of the train. | EFB-RS-418 | The draining points in the condenser area will be designed in order to correctly drain at least 1.5 times Z, all along the life of the train. | 100 | C |  | C
EFB-RS-419 | The draining points in the fresh air inlet area will be designed in order to correctly drain at least 1.5 times Y, all along the life of the train. | EFB-RS-419 | The draining points in the fresh air inlet area will be designed in order to correctly drain at least 1.5 times Y, all along the life of the train. | 100 | C |  | C
EFB-RS-420 | The size and number of draining points will be decided in order to avoid stagnant water inside the HVAC unit in the most severe conditions (not in the evaporator area, nor in the condenser area, neither in the fresh air inlet area). | EFB-RS-420 | The size and number of draining points will be decided in order to avoid stagnant water inside the HVAC unit in the most severe conditions (not in the evaporator area, nor in the condenser area, neither in the fresh air inlet area). | 100 | C |  | C
EFB-RS-421 | The number and size of the draining points in the HVAC system will be defined during the tender stage. | EFB-RS-421 | The number and size of the draining points in the HVAC system will be defined during the tender stage. | 100 | C |  | C
EFB-RS-422 | The Supplier will provide during the tender stage the overpressure or underpressure value of each of the draining points: - Condenser areas - Evaporator areas - Fresh air inlet areas | EFB-RS-422 | The Supplier will provide during the tender stage the overpressure or underpressure value of each of the draining points: - Condenser areas - Evaporator areas - Fresh air inlet areas | 100 | C | HC_230517: Condenser : +100Pa Evaporator: -350 Pa Fresh air inlets: -10 Pa | C | HC_230517: Condenser : +100Pa Evaporator: -350 Pa Fresh air inlets: -10 Pa
EFB-RS-423 | The Supplier will confirm which is the maximum height of water considered in the evaporator and in the condenser area when the train is in the highest gradient and in the highest cant . The height of the draining pans will be higher than this, to avoid the collected water spilling independently of the state of the train or the track. | EFB-RS-423 | The Supplier will confirm which is the maximum height of water considered in the evaporator and in the condenser area when the train is in the highest gradient and in the highest cant . The height of the draining pans will be higher than this, to avoid the collected water spilling independently of the state of the train or the track. | 100 | NC | HC_230517: It does not seem critical because there is height to put the necessary draining pans, but concrete data is needed to confirm. We will make the standard design a priori. This information will be detailed in the development phase of the project, when the detailed design is carried out and the necessary specifications are known (maximum slope, gradients, etc ...) " Maximum gradient = 6.5%. Maximum cant in curve = 180 mm. this data would be taken into account for the detail design during the project development | NC | HC_230517: It does not seem critical because there is height to put the necessary draining pans, but concrete data is needed to confirm. We will make the standard design a priori. This information will be detailed in the development phase of the project, when the detailed design is carried out and the necessary specifications are known (maximum slope, gradients, etc ...) " Maximum gradient = 6.5%. Maximum cant in curve = 180 mm. this data would be taken into account for the detail design during the project development
EFB-RS-424 | A condensate drain pan equipped with internal baffles shall be provided beneath the evaporator coil, headers, thermal expansion valves, and coil "U"-bends in order to collect condensation. | EFB-RS-424 | A condensate drain pan equipped with internal baffles shall be provided beneath the evaporator coil, headers, thermal expansion valves, and coil "U"-bends in order to collect condensation. | 100 | C |  | C
EFB-RS-425 | The drainage shall be so designed to eliminate the requirement for unblocking of leaves and other debris. | EFB-RS-425 | The drainage shall be so designed to eliminate the requirement for unblocking of leaves and other debris. | 100 | C |  | C
EFB-RS-426 | The Supplier will confirm during the tender which are the actions considered in the design as to avoid the draining points of the HVAC being blocked. | EFB-RS-426 | The Supplier will confirm during the tender which are the actions considered in the design as to avoid the draining points of the HVAC being blocked. | 100 | C |  | C
EFB-RS-427 | The Supplier will explain during the tender how to access to the HVAC system as to clean and to visually inspect the draining holes are not blocked. | EFB-RS-427 | The Supplier will explain during the tender how to access to the HVAC system as to clean and to visually inspect the draining holes are not blocked. | 100 | C |  | C
EFB-RS-428 | Condensate drains and piping shall be designed to provide unrestricted drainage and a sufficient standing water column or approved water retention device to prevent reverse air flow drainage restriction due to the air pressure differential between the drain pan and the condensate outlet. The Supplier will explain during the tender stage the solution proposed for this. | EFB-RS-428 | Condensate drains and piping shall be designed to provide unrestricted drainage and a sufficient standing water column or approved water retention device to prevent reverse air flow drainage restriction due to the air pressure differential between the drain pan and the condensate outlet. The Supplier will explain during the tender stage the solution proposed for this. | 100 | C |  | C
EFB-RS-429 | The condensate drain lines, coil housing, and pan shall be insulated to prevent condensation formation. | EFB-RS-429 | The condensate drain lines, coil housing, and pan shall be insulated to prevent condensation formation. | 100 | C |  | C
EFB-RS-430 | When the unit operates or is idle, necessary precautions shall be taken to prevent the incoming of rain water with the sucked air or from the lid gaskets and connection bolts of the unit. In any case, the design of the draining system must consider that any water can get from the fresh air intake, from the gaskets and connection bolts, so solutions to drain this water must be applied. | EFB-RS-430 | When the unit operates or is idle, necessary precautions shall be taken to prevent the incoming of rain water with the sucked air or from the lid gaskets and connection bolts of the unit. In any case, the design of the draining system must consider that any water can get from the fresh air intake, from the gaskets and connection bolts, so solutions to drain this water must be applied. | 100 | C |  | C
EFB-RS-431 | The draining solution shall be designed to be conducted in order to throw the water directly on the underframe as for the fresh air, as for the evaporator area, as for the condenser area. | EFB-RS-431 | The draining solution shall be designed to be conducted in order to throw the water directly on the underframe as for the fresh air, as for the evaporator area, as for the condenser area. | 100 | C |  | C
EFB-RS-432 | The Supplier will confirm during the tender stage if any syphon or duck peak shall be fitted in the draining pipes in order to avoid the evaporator fan sucking the condensed water while the fan is running and thus not enabling a correct draining. | EFB-RS-432 | The Supplier will confirm during the tender stage if any syphon or duck peak shall be fitted in the draining pipes in order to avoid the evaporator fan sucking the condensed water while the fan is running and thus not enabling a correct draining. | 100 | C | HC_230517: a solution based on duck peaks is proposed | C | HC_230517: a solution based on duck peaks is proposed
EFB-RS-434 | The HVAC system shall automatically switch over to emergency ventilation in case AC power is completely lost. In this case, ventilation powered by the battery shall be available to keep, the CO2 concentration below 10.000 PPM for at least 60 minutes, without opening windows or doors, assuming maximum passenger load. | EFB-RS-434 | The HVAC system shall automatically switch over to emergency ventilation in case AC power is completely lost. In this case, ventilation powered by the battery shall be available to keep, the CO2 concentration below 10.000 PPM for at least 60 minutes, without opening windows or doors, assuming maximum passenger load. | 100 | C | HC_230517: DC Ventilator are considered | C | HC_230517: DC Ventilator are considered
EFB-RS-435 | In emergency ventilation mode the evaporator fan speed will be adjusted to allow just the necessary air flow, rather than the normal (return + fresh) air flow. | EFB-RS-435 | In emergency ventilation mode the evaporator fan speed will be adjusted to allow just the necessary air flow, rather than the normal (return + fresh) air flow. | 100 | C |  | C
EFB-RS-436 | During emergency ventilation the fresh air damper will be fully open to maximize the fresh air flow rate with minimum load on the batteries. | EFB-RS-436 | During emergency ventilation the fresh air damper will be fully open to maximize the fresh air flow rate with minimum load on the batteries. | 100 | C |  | C
EFB-RS-438 | The HVAC controller will send a signal to the TCMS to inform it is operating in emergency ventilation condition. | EFB-RS-438 | The HVAC controller will send a signal to the TCMS to inform it is operating in emergency ventilation condition. | 100 | C |  | C
EFB-RS-441 | The HVAC system will blow the conditioned air vertically, though two holes in the botton area of the evaporator side. The Supplier shall propose the dimensions of the air supply connections during the tender stage. | EFB-RS-441 | The HVAC system will blow the conditioned air vertically, though two holes in the botton area of the evaporator side. The Supplier shall propose the dimensions of the air supply connections during the tender stage. | 100 | C |  | C
EFB-RS-442 | The HVAC system will return the saloon air vertically, through one centered hole in the bottom area of the unit. | EFB-RS-442 | The HVAC system will return the saloon air vertically, through one centered hole in the bottom area of the unit. | 100 | C |  | C
EFB-RS-443 | In order to not exceed the static envelope the HVAC system will be mounted in the transversal space envelope indicated in drawing in appendix 1. Drainings and tolerances must be considered in this envelope as well. Also the locks for the covers. The fixations of the HVAC unit shall be designed in order to be compatible with the fixing rails in that drawing. The insulation material of the Saloon HVAC system will be considered as well in this space envelope. | EFB-RS-443 | In order to not exceed the static envelope the HVAC system will be mounted in the transversal space envelope indicated in drawing in appendix 1. Drainings and tolerances must be considered in this envelope as well. Also the locks for the covers. The fixations of the HVAC unit shall be designed in order to be compatible with the fixing rails in that drawing. The insulation material of the Saloon HVAC system will be considered as well in this space envelope. | 100 | C |  | C
EFB-RS-444 | The external insulation material of the Saloon HVAC system in the embedded part of the HVAC unit will provide an isolation level equivalent to the isolation of the carbody. The Supplier will confirm during the tender stage the thickness of the considered isolation material and its isolation level. | EFB-RS-444 | The external insulation material of the Saloon HVAC system in the embedded part of the HVAC unit will provide an isolation level equivalent to the isolation of the carbody. The Supplier will confirm during the tender stage the thickness of the considered isolation material and its isolation level. | 100 | NA | HC_230517: NA the HVAC unit have not embedded part, is totally over roof | NA | HC_230517: NA the HVAC unit have not embedded part, is totally over roof
EFB-RS-445 | The HVAC unit will be fitted with fixing supports only in the longitudinal direction. | EFB-RS-445 | The HVAC unit will be fitted with fixing supports only in the longitudinal direction. | 100 | C |  | C
EFB-RS-446 | The interface between the HVAC system and the car roof structure will be completely sealed against penetration of water into the saloon. Double sealing barrier will be considered. Gaskets for the sealing barrier will be chosen and provided by the Supplier, installed in the HVAC system, and will provide a completely sealed interface as when the train is stationary as when the train is at maximum speed with maximum vibrations. | EFB-RS-446 | The interface between the HVAC system and the car roof structure will be completely sealed against penetration of water into the saloon. Double sealing barrier will be considered. Gaskets for the sealing barrier will be chosen and provided by the Supplier, installed in the HVAC system, and will provide a completely sealed interface as when the train is stationary as when the train is at maximum speed with maximum vibrations. | 100 | C |  | C
EFB-RS-448 | The Supplier will be responsible of providing a completely sealed interface even though maximum tolerances of the roof frame. | EFB-RS-448 | The Supplier will be responsible of providing a completely sealed interface even though maximum tolerances of the roof frame. | 100 | C |  | C
EFB-RS-449 | The Supplier shall provide during the tender stage the dimensions of all the components in the scope of supply. | EFB-RS-449 | The Supplier shall provide during the tender stage the dimensions of all the components in the scope of supply. | 100 | C |  | C
EFB-RS-450 | The control panel of each HVAC unit shall be located inside the HVAC equipment. | EFB-RS-450 | The control panel of each HVAC unit shall be located inside the HVAC equipment. | 100 | C |  | C
EFB-RS-451 | All auxiliary elements (screws, washers…) that are under CAF supply shall be defined by supplier. | EFB-RS-451 | All auxiliary elements (screws, washers…) that are under CAF supply shall be defined by supplier. | 100 | C |  | C
EFB-RS-452 | System components that might generate vibrations must be fastened in the box by elastic elements and must be of easy access for inspection and maintenance services. | EFB-RS-452 | System components that might generate vibrations must be fastened in the box by elastic elements and must be of easy access for inspection and maintenance services. | 100 | C |  | C
EFB-RS-453 | The Supplier shall submit a calculation summary or FEM calculation or test reports, in order to verify the correct dimensioning of the HVAC Equipment case (considering the specified efforts). | EFB-RS-453 | The Supplier shall submit a calculation summary or FEM calculation or test reports, in order to verify the correct dimensioning of the HVAC Equipment case (considering the specified efforts). | 100 | C |  | C
EFB-RS-454 | The Supplier shall confirm during the tender stage the proposed material for the saloon HVAC frame and covers. Painted aluminium or stainless steel could be acceptable. Any proposed solution shall comply with the corrosion protection requirements. | EFB-RS-454 | The Supplier shall confirm during the tender stage the proposed material for the saloon HVAC frame and covers. Painted aluminium or stainless steel could be acceptable. Any proposed solution shall comply with the corrosion protection requirements. | 100 | C | HC_230303: Painted AL is considered | C | HC_230303: Painted AL is considered
EFB-RS-455 | The Supplier shall define during the tender stage the proposed IP degree according IEC 60529 of main components, including its connections: - Control Unit - Compressors - Evaporator motors - Condenser motors - Solenoid valves - Overhead heaters - Motors of the heat convectors - Heaters of the heat convectors | EFB-RS-455 | The Supplier shall define during the tender stage the proposed IP degree according IEC 60529 of main components, including its connections: - Control Unit - Compressors - Evaporator motors - Condenser motors - Solenoid valves - Overhead heaters - Motors of the heat convectors - Heaters of the heat convectors | 100 | C | HC_230517: Control Unit IP20 Compressors: IP55 evaporator FAN. IP55 condenser fan: IP54 Solenoid vales: IP67 Al heaters and components ; IP20 | C | HC_230517: Control Unit IP20 Compressors: IP55 evaporator FAN. IP55 condenser fan: IP54 Solenoid vales: IP67 Al heaters and components ; IP20
EFB-RS-456 | The supplier should define and send the installation instructions of the HVAC. Release the assembly instructions to the Portal. | EFB-RS-456 | The supplier should define and send the installation instructions of the HVAC. Release the assembly instructions to the Portal. | 100 | C |  | C
EFB-RS-457 | The equipment can be removed from the exterior of the upper part. The arrangement of this equipment allows easy access for major maintenance operations. | EFB-RS-457 | The equipment can be removed from the exterior of the upper part. The arrangement of this equipment allows easy access for major maintenance operations. | 100 | C |  | C
EFB-RS-458 | The main elements of the air conditioning installation, as well as the equipment box, will be mounted with elastic mounts in order to attenuate vibrations and noise. | EFB-RS-458 | The main elements of the air conditioning installation, as well as the equipment box, will be mounted with elastic mounts in order to attenuate vibrations and noise. | 100 | C |  | C
EFB-RS-464 | Any fault in the communication bus will not affect to the regulation of the electronic controller, so the HVAC system could be working in ventilation, full cooling, partial cooling or any working mode according to the default regulation curve. | EFB-RS-464 | Any fault in the communication bus will not affect to the regulation of the electronic controller, so the HVAC system could be working in ventilation, full cooling, partial cooling or any working mode according to the default regulation curve. | 100 | C | HC_230517: To be agreed in design stage. In any case, it would not be possible to activate full_cooling since we cannot offset the compressors activations ("comp_enable" signal), and we also do not know if we have AC power ("AC = ON" signal). We usually done is to set a Ventilation point, it is the standard and our proposal In case of communication failure, the system can work in full cooling mode assuming the risk of some peaks at same time. To be defined during design stage. | C | HC_230517: To be agreed in design stage. In any case, it would not be possible to activate full_cooling since we cannot offset the compressors activations ("comp_enable" signal), and we also do not know if we have AC power ("AC = ON" signal). We usually done is to set a Ventilation point, it is the standard and our proposal In case of communication failure, the system can work in full cooling mode assuming the risk of some peaks at same time. To be defined during design stage.
EFB-RS-465 | The HVAC controller will send a FAULT signal to the TCMS in case of any degraded condition. | EFB-RS-465 | The HVAC controller will send a FAULT signal to the TCMS in case of any degraded condition. | 100 | C |  | C
EFB-RS-467 | All procedures, equipment and personnel needed to carry out any test will be provided by the supplier. | EFB-RS-467 | All procedures, equipment and personnel needed to carry out any test will be provided by the supplier. | 100 | C |  | C
EFB-RS-468 | If it would be required to overcome these trials, the supplier should carry out the necessary changes on his equipment for this purpose and repeat the tests. | EFB-RS-468 | If it would be required to overcome these trials, the supplier should carry out the necessary changes on his equipment for this purpose and repeat the tests. | 100 | C |  | C
EFB-RS-469 | Identical equipment that had conducted identical type test before successfully are exempt. In such cases protocols and results of those tests must be submitted. | EFB-RS-469 | Identical equipment that had conducted identical type test before successfully are exempt. In such cases protocols and results of those tests must be submitted. | 100 | C |  | C
EFB-RS-470 | The Supplier shall define during the tender stage the number of tests foreseen to do and the number of tests that will be proposed to be waived providing reports of previous tests. | EFB-RS-470 | The Supplier shall define during the tender stage the number of tests foreseen to do and the number of tests that will be proposed to be waived providing reports of previous tests. | 100 | C |  | C
EFB-RS-471 | The correct dimensioning of the circuit breakers and thermal protections shall be tested during the type test in the climatic chamber at Supplier's facilities. During these tests and being the system at maximum and minimum temperatures, sudden starts and stops of the equipment shall be forced, in order to validate the correct dimensioning of the protections. | EFB-RS-471 | The correct dimensioning of the circuit breakers and thermal protections shall be tested during the type test in the climatic chamber at Supplier's facilities. During these tests and being the system at maximum and minimum temperatures, sudden starts and stops of the equipment shall be forced, in order to validate the correct dimensioning of the protections. | 100 | C |  | C
EFB-RS-472 | The passenger climate control system shall be tested in accordance with EN 14750-2. Test level TL2. | EFB-RS-472 | The passenger climate control system shall be tested in accordance with EN 14750-2. Test level TL2. | 100 | C | HC_230517: TL1 considered in the initial offer. Assistance for TL2 will be quoted separately | C | HC_230517: TL1 considered in the initial offer. Assistance for TL2 will be quoted separately
EFB-RS-473 | The Supplier shall collaborate with CAF in the preliminary tests that will be done in Beasain at car level in advance to the official tests, in order to try to validate the compliance with the EN 14750-2 test level TL2 , as finally applicable, in CAF factory. The Supplier shall assist to these preliminary tests, and shall assist also to the official tests in the climatic chamber. | EFB-RS-473 | The Supplier shall collaborate with CAF in the preliminary tests that will be done in Beasain at car level in advance to the official tests, in order to try to validate the compliance with the EN 14750-2 test level TL2 , as finally applicable, in CAF factory. The Supplier shall assist to these preliminary tests, and shall assist also to the official tests in the climatic chamber. | 100 | C | HC_230517: Preliminary test will be according the standard HC procedure, similar to a evalution TL1. Assistance for TL2 will be quoted separately. | C | HC_230517: Preliminary test will be according the standard HC procedure, similar to a evalution TL1. Assistance for TL2 will be quoted separately.
EFB-RS-474 | Additionally the Supplier will be responsible of including following tests in the test specification and doing these type test in factory CAF together with the CAF personnel, in order to demonstrate the correct design of the drainage of the HVAC system once mounted in the train. A proposal for these test will be as follows. Part 1. Test with the HVAC system completely stopped: 1.a) Throw a water flow of 1.5 times X(l/min) in the evaporator drain pan. Check that all the draining ports open, and no water is stagnant in the pan. Check that there is not any water leak in the joinings between the HVAC system and the train draining pipework. 1.b) Throw a water flow of 1.5 times Z(l/min) in the condenser drain pan. Check that all the draining ports open, and no water is stagnant in the pan. Check that there is not any water leak in the joinings between the HVAC system and the train draining pipework. 1.c) Throw a water flow of 1.5 times Y(l/min) in the fresh air inlet. Check that all the draining ports open, and no water is stagnant in the pan. Check that there is not any water leak in the joinings between the HVAC system and the train draining pipework. Part 2: Test with the HVAC system in maximum cooling mode 2.a) Throw a water flow of 1.5 times X(l/min) in the evaporator drain pan. Check that all the water is drained correctly and no water is dripping in the supply air ducting or the passenger area. 2.b) Throw a water flow of 1.5 times Z(l/min) in the condenser drain pan. Check that all the water is drained correctly and no water is dripping in the passenger area. 2.c) Throw a water flow of 1.5 times Y(l/min) in the fresh air inlet. Check that all the water is drained correctly and no water is dripping in the supply air ducting or the passenger area. | EFB-RS-474 | Additionally the Supplier will be responsible of including following tests in the test specification and doing these type test in factory CAF together with the CAF personnel, in order to demonstrate the correct design of the drainage of the HVAC system once mounted in the train. A proposal for these test will be as follows. Part 1. Test with the HVAC system completely stopped: 1.a) Throw a water flow of 1.5 times X(l/min) in the evaporator drain pan. Check that all the draining ports open, and no water is stagnant in the pan. Check that there is not any water leak in the joinings between the HVAC system and the train draining pipework. 1.b) Throw a water flow of 1.5 times Z(l/min) in the condenser drain pan. Check that all the draining ports open, and no water is stagnant in the pan. Check that there is not any water leak in the joinings between the HVAC system and the train draining pipework. 1.c) Throw a water flow of 1.5 times Y(l/min) in the fresh air inlet. Check that all the draining ports open, and no water is stagnant in the pan. Check that there is not any water leak in the joinings between the HVAC system and the train draining pipework. Part 2: Test with the HVAC system in maximum cooling mode 2.a) Throw a water flow of 1.5 times X(l/min) in the evaporator drain pan. Check that all the water is drained correctly and no water is dripping in the supply air ducting or the passenger area. 2.b) Throw a water flow of 1.5 times Z(l/min) in the condenser drain pan. Check that all the water is drained correctly and no water is dripping in the passenger area. 2.c) Throw a water flow of 1.5 times Y(l/min) in the fresh air inlet. Check that all the water is drained correctly and no water is dripping in the supply air ducting or the passenger area. | 100 | NA | HC_230517:These tess are included in Z4 position factory test by CAF, and performed by CAF, just in case of problems detected during the testing HC will be inform and call to give support. NA, because it's done in Z4. This test is also done in the origin type test, but this is not what is described in this requirement. this requirement refers to the factory type test, and generally this test is carried out in the earliest project phase possible, normally at same time than Z4 test (carried out by CAF). Later, during the Factory Type test, the drainage system is checked again during the cooling test. In any case, HC will always support CAF if necessary. | NA | HC_230517:These tess are included in Z4 position factory test by CAF, and performed by CAF, just in case of problems detected during the testing HC will be inform and call to give support. NA, because it's done in Z4. This test is also done in the origin type test, but this is not what is described in this requirement. this requirement refers to the factory type test, and generally this test is carried out in the earliest project phase possible, normally at same time than Z4 test (carried out by CAF). Later, during the Factory Type test, the drainage system is checked again during the cooling test. In any case, HC will always support CAF if necessary.
EFB-RS-475 | The Supplier shall also demonstrate during the type test in origin the HVAC system complies with the performances in section "3.1 Performance". If not specifically agreed with CAF the type tests at origin will include all the operating conditions in the datasheet. | EFB-RS-475 | The Supplier shall also demonstrate during the type test in origin the HVAC system complies with the performances in section "3.1 Performance". If not specifically agreed with CAF the type tests at origin will include all the operating conditions in the datasheet. | 100 | NC | HC_230517:To be discuss. Precooling, preheating, emergency vetilation, etc... can not be make in origyn type test. Performance Heating test in different conditions makes no senses since the capacity only depends on the resitors value. Not all calculations are tested since many of them are limited bu the testing conditions. It should be agreed how many. The idea is to follow a similar level than the TL1 of EN14750. The test to be performed during type test will be agreed during the design phase and based on the TL2 level of 14750 standard. All protocol and test performed are agreed during the design phase, Origin and factory test, and all of them are based in the EN 14750 standard. | NC | HC_230517:To be discuss. Precooling, preheating, emergency vetilation, etc... can not be make in origyn type test. Performance Heating test in different conditions makes no senses since the capacity only depends on the resitors value. Not all calculations are tested since many of them are limited bu the testing conditions. It should be agreed how many. The idea is to follow a similar level than the TL1 of EN14750. The test to be performed during type test will be agreed during the design phase and based on the TL2 level of 14750 standard. All protocol and test performed are agreed during the design phase, Origin and factory test, and all of them are based in the EN 14750 standard.
EFB-RS-476 | During the project phase, CAF will present a complete technical study and carry out preliminary tests on finished cars or those in an advanced state of construction. The tests carried out will be those that are necessary to ensure and demonstrate that the installation meets the required performance, in accordance with EN14750-TL2. | EFB-RS-476 | During the project phase, CAF will present a complete technical study and carry out preliminary tests on finished cars or those in an advanced state of construction. The tests carried out will be those that are necessary to ensure and demonstrate that the installation meets the required performance, in accordance with EN14750-TL2. | 100 | NA | HC_230517: tests to be permofed in CAF facilites at Z4 division during the project stage. | NA | HC_230517: tests to be permofed in CAF facilites at Z4 division during the project stage.
EFB-RS-478 | The Supplier will provide a list of the special test equipment required for maintenance, repair, troubleshooting, and diagnostics. This shall include equipment for charging, refrigerant recovery, evacuation, frame for HVAC lifting (if required) and other repairs. | EFB-RS-478 | The Supplier will provide a list of the special test equipment required for maintenance, repair, troubleshooting, and diagnostics. This shall include equipment for charging, refrigerant recovery, evacuation, frame for HVAC lifting (if required) and other repairs. | 100 | C |  | C
EFB-RS-479 | The special test equipment defined in the requirement above shall be provided by the HVAC system Supplier. | EFB-RS-479 | The special test equipment defined in the requirement above shall be provided by the HVAC system Supplier. | 100 | C |  | C
EFB-RS-480 | CAF forsees that it won't be possible to measure the supply air-flow as the sum of fresh air-flow and return due to the lack of access to the return of the HVAC from the inside of the saloon during the comfort tests. Therefore, it will be necessary to measure the supply air-flow in the HVAC unit evaporator using a different methodology. There are two procedures CAF is familiar with in this sense: / Installing a calibrated nozzle in the evaporator fan and determining the supply air-flow by measurement of pressure difference. The calibrated nozzle should be provided by the supplier of the evaporator fan. / Characterize the pressure losses in the heat exchanger of the evaporator as a function of the supply air-flow during origin tests of the HVAC unit. During climatic tests the supply air-flow will be determined with a pressure-drop measurement according to the data obtained during origin tests. If there is another valid procedures to determine supply air-flow, it will be analyzed. | EFB-RS-480 | CAF forsees that it won't be possible to measure the supply air-flow as the sum of fresh air-flow and return due to the lack of access to the return of the HVAC from the inside of the saloon during the comfort tests. Therefore, it will be necessary to measure the supply air-flow in the HVAC unit evaporator using a different methodology. There are two procedures CAF is familiar with in this sense: / Installing a calibrated nozzle in the evaporator fan and determining the supply air-flow by measurement of pressure difference. The calibrated nozzle should be provided by the supplier of the evaporator fan. / Characterize the pressure losses in the heat exchanger of the evaporator as a function of the supply air-flow during origin tests of the HVAC unit. During climatic tests the supply air-flow will be determined with a pressure-drop measurement according to the data obtained during origin tests. If there is another valid procedures to determine supply air-flow, it will be analyzed. | 100 | C | HC_230517: The air flow will be measure Installing a calibrated nozzle in the evaporator fan and determining the supply air-flow by measurement of pressure difference. | C | HC_230517: The air flow will be measure Installing a calibrated nozzle in the evaporator fan and determining the supply air-flow by measurement of pressure difference.
EFB-RS-484 | Smoke detectors are not foreseen in the fresh air intake. Smoke detector shall be considered in the return air intake as an OPTION 3 | EFB-RS-484 | Smoke detectors are not foreseen in the fresh air intake. Smoke detector shall be considered in the return air intake as an OPTION 3 | 100 | C |  | C
EFB-RS-487 | The design of this equipment guarantees a low aerodynamic impact and ensures watertightness between the equipment and the carbody. | EFB-RS-487 | The design of this equipment guarantees a low aerodynamic impact and ensures watertightness between the equipment and the carbody. | 100 | C |  | C
EFB-RS-488 | The equipment are mounted on brackets welded onto the Train structure, with the insertion of a resilient mount that will prevent the transmission of vibrations to the carbody. The compressor will be fixed onto the frame of the appropriate module, by means of a resilient mount. | EFB-RS-488 | The equipment are mounted on brackets welded onto the Train structure, with the insertion of a resilient mount that will prevent the transmission of vibrations to the carbody. The compressor will be fixed onto the frame of the appropriate module, by means of a resilient mount. | 100 | C |  | C
EFB-RS-489 | The equipment is removable from the outside of the upper part. The arrangement of this equipment allows easy access for the main maintenance operations. | EFB-RS-489 | The equipment is removable from the outside of the upper part. The arrangement of this equipment allows easy access for the main maintenance operations. | 100 | C |  | C
EFB-RS-490 | The cooling circuit system is equipped with sectioning by means of valves, which makes it possible to replace the compressors without draining the system. | EFB-RS-490 | The cooling circuit system is equipped with sectioning by means of valves, which makes it possible to replace the compressors without draining the system. | 100 | C | HC_230517: Same concept than AMYA project will be used | C | HC_230517: Same concept than AMYA project will be used
EFB-RS-491 | The electrical power supply of the equipment and its components has the appropriate electrical protections (circuit breakers, differential, etc.). The main HVAC electrical equipment has its own individual protections. All other electrical components (relays, coils, etc.) have collective protection. The electrical protections of the listed components of the HVAC equipment are easily accessible from inside the train without the need to climb onto the roof. Access to these protections is via trapdoors which are opened by means of a square key. | EFB-RS-491 | The electrical power supply of the equipment and its components has the appropriate electrical protections (circuit breakers, differential, etc.). The main HVAC electrical equipment has its own individual protections. All other electrical components (relays, coils, etc.) have collective protection. The electrical protections of the listed components of the HVAC equipment are easily accessible from inside the train without the need to climb onto the roof. Access to these protections is via trapdoors which are opened by means of a square key. | 100 | C |  | C
EFB-RS-492 | The necessary items are provided for the collection, conveyance and drainage of condensates to the undercar area of the train. | EFB-RS-492 | The necessary items are provided for the collection, conveyance and drainage of condensates to the undercar area of the train. | 100 | NA |  | NA
EFB-RS-493 | Air impelled into the passenger saloons is previously treated in the HVAC equipment, to ensure passenger climatic comfort. This air is blown through the entire length of the vehicle and evenly distributed via the ducts which are made up of two sections, primary and secondary, thus ensuring sensation of comfort. | EFB-RS-493 | Air impelled into the passenger saloons is previously treated in the HVAC equipment, to ensure passenger climatic comfort. This air is blown through the entire length of the vehicle and evenly distributed via the ducts which are made up of two sections, primary and secondary, thus ensuring sensation of comfort. | 100 | NA |  | NA
EFB-RS-494 | Air-conditioned supply air is provided in the passenger access vestibule areas to reduce the effect of opening passenger access doors. The train is equipped with floor convectors throughout the passenger saloon to improve warm air distribution and passenger comfort. The installation of convectors on the floor and the distribution of air on the ceiling reduce the effect from the opening the passenger access doors to the outside environment. | EFB-RS-494 | Air-conditioned supply air is provided in the passenger access vestibule areas to reduce the effect of opening passenger access doors. The train is equipped with floor convectors throughout the passenger saloon to improve warm air distribution and passenger comfort. The installation of convectors on the floor and the distribution of air on the ceiling reduce the effect from the opening the passenger access doors to the outside environment. | 100 | C |  | C
EFB-RS-495 | There is no direct communication between the supply air and the return air, and between the foul exhaust air and the exterior fresh air. | EFB-RS-495 | There is no direct communication between the supply air and the return air, and between the foul exhaust air and the exterior fresh air. | 100 | C |  | C
EFB-RS-496 | The car HVAC system can operate at least in the following operating modes, to be selected by means of a selector switch provided in the driver cabs: | EFB-RS-496 | The car HVAC system can operate at least in the following operating modes, to be selected by means of a selector switch provided in the driver cabs: | 100 | C |  | C
EFB-RS-497 | - HVAC switched off. | EFB-RS-497 | - HVAC switched off. | 100 | C |  | C
EFB-RS-498 | - Ventilation Operation. | EFB-RS-498 | - Ventilation Operation. | 100 | C |  | C
EFB-RS-499 | - HVAC in operation. Automatic operation. | EFB-RS-499 | - HVAC in operation. Automatic operation. | 100 | C |  | C
EFB-RS-500 | - Maximum renovation mode. | EFB-RS-500 | - Maximum renovation mode. | 100 | C |  | C
EFB-RS-501 | The HVAC system is redundant in each passenger car and in all aspects (thermodynamic and electronic). In the event of a breakdown of any element (of any kind), at least 50% of the HVAC is available in each car. | EFB-RS-501 | The HVAC system is redundant in each passenger car and in all aspects (thermodynamic and electronic). In the event of a breakdown of any element (of any kind), at least 50% of the HVAC is available in each car. | 100 | C |  | C
EFB-RS-503 | All HVAC equipment can work under normal conditions with exterior ambient temperatures Class T3 according to the UNE EN 50125-1 standard, between -25ºC and +45ºC. The HVAC system is operational when the temperature of the outside air entering the condenser units reaches 55ºC. | EFB-RS-503 | All HVAC equipment can work under normal conditions with exterior ambient temperatures Class T3 according to the UNE EN 50125-1 standard, between -25ºC and +45ºC. The HVAC system is operational when the temperature of the outside air entering the condenser units reaches 55ºC. | 100 | C |  | C
EFB-RS-504 | The HVAC units are designed for maximum energy efficiency. In this respect, the equipment has the following functionalities: | EFB-RS-504 | The HVAC units are designed for maximum energy efficiency. In this respect, the equipment has the following functionalities: | 100 | C |  | C
EFB-RS-505 | The HVAC units have a "free-cooling" operation mode, which is designed such that the required comfort conditions are maintained through air renewal (without starting the compressors of the units) when cooling is required and the outside temperature allows it. This mode is automatically activated when the equipment is operating in automatic HVAC-operation mode and the conditions are suitable. | EFB-RS-505 | The HVAC units have a "free-cooling" operation mode, which is designed such that the required comfort conditions are maintained through air renewal (without starting the compressors of the units) when cooling is required and the outside temperature allows it. This mode is automatically activated when the equipment is operating in automatic HVAC-operation mode and the conditions are suitable. | 100 | C |  | C
EFB-RS-506 | The air HVAC units have a "car-by-car energy saving" operating mode which, depending on the interior air quality analysed by the CO2 sensors (a parameter dependent on the passenger occupancy of the car), optimises the fresh air flow. Therefore, in the event of a failure of both the CO2 sensor and the fresh air control dampers, the system switches to a safe state, guaranteeing a minimum flow of fresh air. | EFB-RS-506 | The air HVAC units have a "car-by-car energy saving" operating mode which, depending on the interior air quality analysed by the CO2 sensors (a parameter dependent on the passenger occupancy of the car), optimises the fresh air flow. Therefore, in the event of a failure of both the CO2 sensor and the fresh air control dampers, the system switches to a safe state, guaranteeing a minimum flow of fresh air. | 100 | C |  | C
EFB-RS-507 | The HVAC systems in each car have heat pump functionality in one of the two thermodynamic circuits. | EFB-RS-507 | The HVAC systems in each car have heat pump functionality in one of the two thermodynamic circuits. | 100 | NA | HC_230517: Only one circuit per HVAC | NA | HC_230517: Only one circuit per HVAC
EFB-RS-508 | The proposed HVAC systems have been designed with efficiency, with the aim, at all times, of adjusting to the HVAC demand required at each moment and guaranteeing comfort, either in normal mode (ajusting according to the number of passengers in the car), or in car-by-car energy saving mode (by averaging the CO2 level). | EFB-RS-508 | The proposed HVAC systems have been designed with efficiency, with the aim, at all times, of adjusting to the HVAC demand required at each moment and guaranteeing comfort, either in normal mode (ajusting according to the number of passengers in the car), or in car-by-car energy saving mode (by averaging the CO2 level). | 100 | C |  | C
EFB-RS-509 | Following the philosophy of the European Union, Regulation (EU) No. 517/2014 of the European Parliament and of the Council of 16 April 2014 on fluorinated greenhouse gases, measures will be adopted to reduce emissions of hydrofluorocarbons (HFCs), and to achieve more climate-friendly technologies in new equipment and products. Coolant R513A with a lower impact than other refrigerant fluids currently used in the railway sector will be used. | EFB-RS-509 | Following the philosophy of the European Union, Regulation (EU) No. 517/2014 of the European Parliament and of the Council of 16 April 2014 on fluorinated greenhouse gases, measures will be adopted to reduce emissions of hydrofluorocarbons (HFCs), and to achieve more climate-friendly technologies in new equipment and products. Coolant R513A with a lower impact than other refrigerant fluids currently used in the railway sector will be used. | 100 | C |  | C
EFB-RS-511 | The following conditions are considered for the calculation of the pre-cooling and pre-heating demand: | EFB-RS-511 | The following conditions are considered for the calculation of the pre-cooling and pre-heating demand: | 100 | C |  | C
EFB-RS-512 | - The speed of the car is considered to be zero. | EFB-RS-512 | - The speed of the car is considered to be zero. | 100 | C |  | C
EFB-RS-513 | - Solar radiation is considered full in pre-cooling. | EFB-RS-513 | - Solar radiation is considered full in pre-cooling. | 100 | C |  | C
EFB-RS-514 | - Solar radiation is considered to be zero in pre-heating. | EFB-RS-514 | - Solar radiation is considered to be zero in pre-heating. | 100 | C |  | C
EFB-RS-515 | - Passenger occupancy is considered zero in both cases. | EFB-RS-515 | - Passenger occupancy is considered zero in both cases. | 100 | C |  | C
EFB-RS-516 | - The access doors remain closed. | EFB-RS-516 | - The access doors remain closed. | 100 | C |  | C
EFB-RS-518 | The HVAC system, operating in pre-heating mode, is capable of reaching an interior temperature of 18°C in less than 60 minutes, starting from an exterior temperature of -5°C and without solar radiation. | EFB-RS-518 | The HVAC system, operating in pre-heating mode, is capable of reaching an interior temperature of 18°C in less than 60 minutes, starting from an exterior temperature of -5°C and without solar radiation. | 100 | C | HC_230517: Result provides in "Calculations to perform" sheet, case 26, 27 and 28 | C | HC_230517: Result provides in "Calculations to perform" sheet, case 26, 27 and 28
EFB-RS-519 | The HVAC system, operating in pre-cooling mode, without the incorporation of exterior air, is capable of reaching an interior temperature of 28ºC in less than 60 minutes, starting from an interior temperature of 40ºC, and maintaining exterior conditions of 40ºC temperature and 43% relative humidity. | EFB-RS-519 | The HVAC system, operating in pre-cooling mode, without the incorporation of exterior air, is capable of reaching an interior temperature of 28ºC in less than 60 minutes, starting from an interior temperature of 40ºC, and maintaining exterior conditions of 40ºC temperature and 43% relative humidity. | 100 | C | HC_230517: Result provides in "Calculations to perform" sheet, case 11 and 12 | C | HC_230517: Result provides in "Calculations to perform" sheet, case 11 and 12
EFB-RS-520 | The following conditions have been considered for the calculation of the cooling and heating demand: | EFB-RS-520 | The following conditions have been considered for the calculation of the cooling and heating demand: | 100 | C |  | C
EFB-RS-521 | - The operating time of the HVAC system is considered to be sixteen hours per day. | EFB-RS-521 | - The operating time of the HVAC system is considered to be sixteen hours per day. | 100 | C |  | C
EFB-RS-522 | - Calculations will be performed for the maximum speed and stationary train condition. | EFB-RS-522 | - Calculations will be performed for the maximum speed and stationary train condition. | 100 | C |  | C
EFB-RS-523 | The HVAC system, operating in cooling mode, has a power capable of maintaining an interior temperature of 25ºC and an interior relative humidity of 41%-52% with an exterior temperature of 40ºC and an exterior relative humidity of 43%, considering: | EFB-RS-523 | The HVAC system, operating in cooling mode, has a power capable of maintaining an interior temperature of 25ºC and an interior relative humidity of 41%-52% with an exterior temperature of 40ºC and an exterior relative humidity of 43%, considering: | 100 | C |  | C
EFB-RS-526 | - full solar radiation on the car (according to EN 14750 800W/m2). | EFB-RS-526 | - full solar radiation on the car (according to EN 14750 800W/m2). | 100 | C |  | C
EFB-RS-527 | The HVAC system, working in heating mode under the required conditions, has the power capable of maintaining an interior temperature of 22ºC, with an exterior temperature of -10ºC, taking into account: | EFB-RS-527 | The HVAC system, working in heating mode under the required conditions, has the power capable of maintaining an interior temperature of 22ºC, with an exterior temperature of -10ºC, taking into account: | 100 | C |  | C
EFB-RS-530 | - no solar radiation in the car. | EFB-RS-530 | - no solar radiation in the car. | 100 | C |  | C
EFB-RS-534 | - Operation in HVAC mode - Automatic operation. | EFB-RS-534 | - Operation in HVAC mode - Automatic operation. | 100 | C |  | C
EFB-RS-535 | § Normal mode | EFB-RS-535 | § Normal mode | 100 | C |  | C
EFB-RS-536 | § Freecooling mode | EFB-RS-536 | § Freecooling mode | 100 | C |  | C
EFB-RS-537 | § Car-by-car energy saving mode | EFB-RS-537 | § Car-by-car energy saving mode | 100 | C |  | C
EFB-RS-538 | - “Maximum renovation” mode | EFB-RS-538 | - “Maximum renovation” mode | 100 | C |  | C
EFB-RS-539 | - Operation in HVAC mode - Automatic operation: | EFB-RS-539 | - Operation in HVAC mode - Automatic operation: | 100 | C |  | C
EFB-RS-540 | The renewal flow rates are set automatically by the equipment. In other words, the system itself establishes the renovation flow rate according to the interior and exterior conditions, in the pursue of the lowest consumption while maintaining interior conditions of comfort and air quality. | EFB-RS-540 | The renewal flow rates are set automatically by the equipment. In other words, the system itself establishes the renovation flow rate according to the interior and exterior conditions, in the pursue of the lowest consumption while maintaining interior conditions of comfort and air quality. | 100 | C |  | C
EFB-RS-541 | The air renewal in "normal mode" (in case of inhibiting the proposed energy saving modes and freecooling) is 10 m3/h per passenger for exterior temperatures between -10ºC and -5ºC, 20 m3/h between -5ºC and 30ºC, 15 m3/h between 30ºC and 40ºC, and 10 m3/h for over 40ºC. | EFB-RS-541 | The air renewal in "normal mode" (in case of inhibiting the proposed energy saving modes and freecooling) is 10 m3/h per passenger for exterior temperatures between -10ºC and -5ºC, 20 m3/h between -5ºC and 30ºC, 15 m3/h between 30ºC and 40ºC, and 10 m3/h for over 40ºC. | 100 | C |  | C
EFB-RS-542 | The fresh air in free-cooling mode is set automatically by the unit. In any case, the renovation dimensioning allows for flow rates of at least 25 m3/h per passenger. | EFB-RS-542 | The fresh air in free-cooling mode is set automatically by the unit. In any case, the renovation dimensioning allows for flow rates of at least 25 m3/h per passenger. | 100 | C |  | C
EFB-RS-543 | In "car-by-car energy saving" operating mode, the renewal flow rate is optimised on the basis of the interior air quality analysed by a CO2 sensor, which can measure the amount of CO2 particles per million in the interior air at any time. This parameter is dependent on the passenger occupancy of the car and the exterior air quality. | EFB-RS-543 | In "car-by-car energy saving" operating mode, the renewal flow rate is optimised on the basis of the interior air quality analysed by a CO2 sensor, which can measure the amount of CO2 particles per million in the interior air at any time. This parameter is dependent on the passenger occupancy of the car and the exterior air quality. | 100 | C | HC_230517: Details to be discussed and agreed during the development of the project. | C | HC_230517: Details to be discussed and agreed during the development of the project.
EFB-RS-544 | In the event that a fault is diagnosed in any of the components of the "free-cooling" or "car-by-car energy saving" modes of operation, the system automatically reconfigures a conventional refurbishment to the values indicated above as "normal mode". | EFB-RS-544 | In the event that a fault is diagnosed in any of the components of the "free-cooling" or "car-by-car energy saving" modes of operation, the system automatically reconfigures a conventional refurbishment to the values indicated above as "normal mode". | 100 | C | HC_230517: Details to be discussed and agreed during the development of the project. Some components could be effect to both modes | C | HC_230517: Details to be discussed and agreed during the development of the project. Some components could be effect to both modes
EFB-RS-545 | The functional details of the system are finalised and submitted to RENFE during the design phase for approval. | EFB-RS-545 | The functional details of the system are finalised and submitted to RENFE during the design phase for approval. | 100 | C |  | C
EFB-RS-546 | “Maximum renovation” mode: | EFB-RS-546 | “Maximum renovation” mode: | 100 | C |  | C
EFB-RS-547 | The aim of this mode is to maximise the amount of fresh air without prioritising the energy efficiency of the system. The details of this mode should be agreed at the project stage. | EFB-RS-547 | The aim of this mode is to maximise the amount of fresh air without prioritising the energy efficiency of the system. The details of this mode should be agreed at the project stage. | 100 | C | HC_230517: Details to be discussed and agreed during the development of the project. | C | HC_230517: Details to be discussed and agreed during the development of the project.
EFB-RS-548 | Also, during the project phase, the way in which this mode of operation is established by the operation crew / maintenance personnel will be established | EFB-RS-548 | Also, during the project phase, the way in which this mode of operation is established by the operation crew / maintenance personnel will be established | 100 | C | HC_230517: Details to be discussed and agreed during the development of the project. | C | HC_230517: Details to be discussed and agreed during the development of the project.
EFB-RS-550 | The main items for the air-conditioning installation, as well as the equipment box, are mounted using elastic mounts to attenuate vibrations and noise. | EFB-RS-550 | The main items for the air-conditioning installation, as well as the equipment box, are mounted using elastic mounts to attenuate vibrations and noise. | 100 | C |  | C
EFB-RS-551 | Noise given off by the Air Conditioning system and air supply, with the car at a standstill, will not exceed 59.9 dB(A). Supporting evidence of this requirement will be given during the project phase. | EFB-RS-551 | Noise given off by the Air Conditioning system and air supply, with the car at a standstill, will not exceed 59.9 dB(A). Supporting evidence of this requirement will be given during the project phase. | 100 | NA | HC_230517: the EN14750 Cat.A specifies 63 dB for the interior noise in the conford area, under regulation mode. The result expected of this test must be define the target of HVAC noise specific test, made with HVAC alone in origin and specific standard EN ISO 9614. In summary, the target of EN14750 Cat.A interior noise is translated to noise level of HVAC alone in ISO 9614. | NA | HC_230517: the EN14750 Cat.A specifies 63 dB for the interior noise in the conford area, under regulation mode. The result expected of this test must be define the target of HVAC noise specific test, made with HVAC alone in origin and specific standard EN ISO 9614. In summary, the target of EN14750 Cat.A interior noise is translated to noise level of HVAC alone in ISO 9614.
EFB-RS-552 | The exterior and return air is filtered through a filter complying with ISO 16890, ensuring a minimum filtering level of ePM10. | EFB-RS-552 | The exterior and return air is filtered through a filter complying with ISO 16890, ensuring a minimum filtering level of ePM10. | 100 | C |  | C
EFB-RS-553 | The proposed filters in the HVAC equipment guarantee the correct operation of the air conditioning equipment as well as the quality of the supply air, so that no additional filters are deemed necessary. | EFB-RS-553 | The proposed filters in the HVAC equipment guarantee the correct operation of the air conditioning equipment as well as the quality of the supply air, so that no additional filters are deemed necessary. | 100 | C |  | C
EFB-RS-554 | During the Project phase, CAF will submit a technical review and conduct the relevant TL2 tests in accordance with the UNE EN 14750 standard to provide evidence that the installation meets the required performance. | EFB-RS-554 | During the Project phase, CAF will submit a technical review and conduct the relevant TL2 tests in accordance with the UNE EN 14750 standard to provide evidence that the installation meets the required performance. | 100 | NA |  | NA
EFB-RS-555 | These performance verification and regulation tests are performed on the finished car in accordance with the EN14750-TL2 standard. They are performed on the most representative car, the cab car. | EFB-RS-555 | These performance verification and regulation tests are performed on the finished car in accordance with the EN14750-TL2 standard. They are performed on the most representative car, the cab car. | 100 | NA |  | NA
EFB-RS-557 | Pressure differences between the interior and exterior, generated by entering a tunnel or by another train passing by, also affect the entry of dust and/or pollen into the carbody through the door system. To mitigate these problems, doors are protected with appropriate door seals. The passenger saloon will also be over-pressurised to ensure that no air can enter from outside without passing through the HVAC equipment. | EFB-RS-557 | Pressure differences between the interior and exterior, generated by entering a tunnel or by another train passing by, also affect the entry of dust and/or pollen into the carbody through the door system. To mitigate these problems, doors are protected with appropriate door seals. The passenger saloon will also be over-pressurised to ensure that no air can enter from outside without passing through the HVAC equipment. | 100 | NA | HC_230303: Door system are out of scope of supply and definition of HC | NA | HC_230303: Door system are out of scope of supply and definition of HC
EFB-RS-560 | - Saloon HVAC equipment: The performance of the HVAC equipment in the event of failure of the various components would be as follows: | EFB-RS-560 | - Saloon HVAC equipment: The performance of the HVAC equipment in the event of failure of the various components would be as follows: | 100 | C |  | C
EFB-RS-563 | - Auxiliary Static Converter: The fault is detected by the auxiliary static converter and performs several retries to recover. If the fault persists, the auxiliary static converter is automatically isolated and the fault is signalled to the driver in the cab. In the event of a failure of an auxiliary static converter, the Train can continue to provide revenue service with 100% of its auxiliary equipment in service, powered by the remaining converter, and an automatic reconfiguration of the equipment takes place. In this case the Train will be able to continue revenue service with no perception of the failure by the passengers, and in no case will the reduction of performance in each and every car lead to HVAC power values below 50% of those indicated in Annex 41 of the DTT (Train Technical Documentation) (B.2.3.13.A "Thermal calculations of the salooon HVAC equipment") and Annex 42 of the DTT (Train Technical Documentation) (B.2.3.13.B "Thermal calculations for the Cab HVAC equipment"). | EFB-RS-563 | - Auxiliary Static Converter: The fault is detected by the auxiliary static converter and performs several retries to recover. If the fault persists, the auxiliary static converter is automatically isolated and the fault is signalled to the driver in the cab. In the event of a failure of an auxiliary static converter, the Train can continue to provide revenue service with 100% of its auxiliary equipment in service, powered by the remaining converter, and an automatic reconfiguration of the equipment takes place. In this case the Train will be able to continue revenue service with no perception of the failure by the passengers, and in no case will the reduction of performance in each and every car lead to HVAC power values below 50% of those indicated in Annex 41 of the TTD (Train Technical Documentation) (B.2.3.13.A "Thermal calculations of the salooon HVAC equipment") and Annex 42 of the TTD (Train Technical Documentation) (B.2.3.13.B "Thermal calculations for the Cab HVAC equipment"). | 100 | NA |  | NA
EFB-RS-567 | The Supplier shall identify, physically, each LRU/SRU with its Manufacturer ID, Part Number (PN), Serial Number (SN) and/or Manufacturing Date (MDF). | EFB-RS-567 | The Supplier shall identify, physically, each LRU/SRU with its Manufacturer ID, Part Number (PN), Serial Number (SN) and/or Manufacturing Date (MDF). | 100 | C |  | C
EFB-RS-568 | Each CI shall be identified physically by a CI’s identification. | EFB-RS-568 | Each CI shall be identified physically by a CI’s identification. | 100 | C |  | C
EFB-RS-569 | The supplier shall identify all configuration items based on the Datamatrix GS1 standard application (ISO 16022, ECC 200) | EFB-RS-569 | The supplier shall identify all configuration items based on the Datamatrix GS1 standard application (ISO 16022, ECC 200) | 100 | C |  | C
EFB-RS-570 | The supplier shall include in the CI identification at least the following fields based on the Datamatrix GS1 standard application (ISO 16022, ECC 200): . (01) GTIN code . (21) Serial number or (10) Batch Number . (241) CAF Code . (11) Manufacturing Date | EFB-RS-570 | The supplier shall include in the CI identification at least the following fields based on the Datamatrix GS1 standard application (ISO 16022, ECC 200): . (01) GTIN code . (21) Serial number or (10) Batch Number . (241) CAF Code . (11) Manufacturing Date | 100 | C |  | C
EFB-RS-571 | All numbering and marks of elements shall be readable and indelible. | EFB-RS-571 | All numbering and marks of elements shall be readable and indelible. | 100 | C |  | C
EFB-RS-572 | The Supplier shall ensure that the CI’s identification position is visible and accessible when the product is disassembled. | EFB-RS-572 | The Supplier shall ensure that the CI’s identification position is visible and accessible when the product is disassembled. | 100 | C | HC_230517. Only for the main plate of the deliverables (not for subcomponents) | C | HC_230517. Only for the main plate of the deliverables (not for subcomponents)
EFB-RS-573 | The CI’s identification shall be visible in the product drawing. | EFB-RS-573 | The CI’s identification shall be visible in the product drawing. | 100 | C |  | C
EFB-RS-574 | The drawing shall specify identification location and its fields. | EFB-RS-574 | The drawing shall specify identification location and its fields. | 100 | C |  | C
EFB-RS-578 | For the design, manufacturing and acceptance of welded components and assemblies, the requirements of the standard series EN 15085-1 to EN 15085-5 are mandatory. CAF reserves the right to require the documentation to prove the compliance of the standard. | EFB-RS-578 | For the design, manufacturing and acceptance of welded components and assemblies, the requirements of the standard series EN 15085-1 to EN 15085-5 are mandatory. CAF reserves the right to require the documentation to prove the compliance of the standard. | 100 | C |  | C
EFB-RS-579 | The Technical Specification C.X1.97.021 defines the "Materials for pneumatic installations" according to the CAF standard. If the supplier proposes any alternative material, different from the CAF standard, the equivalence and compliance of the material must be demonstrated and the supplier shall provide all the proofs necessary for their validation by the Customer. | EFB-RS-579 | The Technical Specification C.X1.97.021 defines the "Materials for pneumatic installations" according to the CAF standard. If the supplier proposes any alternative material, different from the CAF standard, the equivalence and compliance of the material must be demonstrated and the supplier shall provide all the proofs necessary for their validation by the Customer. | 100 | NA |  | NA
EFB-RS-580 | The painting system shall comply with the requirements established in the standards NF F 19-141-1 and NF F 19-141-2. CAF reserves the right to require documentation to prove compliance. Alternatively, CAF´s painting system may be used. | EFB-RS-580 | The painting system shall comply with the requirements established in the standards NF F 19-141-1 and NF F 19-141-2. CAF reserves the right to require documentation to prove compliance. Alternatively, CAF´s painting system may be used. | 100 | NC | HC_230517: Painting system proposed and approved by CAF is: •“Sist. nº 2 Polvo. Fermupe: “Desengrase +desmutting Alumal Deox 445 + pasivado Alumal Bond 701 + acabado Adpata Color ADAPTA PES –RS Ó RM - gama VIVENDI". Pintura en polvo de Adapta de Fermupe. Colour and Gloss according agreed previous projects | NC | HC_230517: Painting system proposed and approved by CAF is: •“Sist. nº 2 Polvo. Fermupe: “Desengrase +desmutting Alumal Deox 445 + pasivado Alumal Bond 701 + acabado Adpata Color ADAPTA PES –RS Ó RM - gama VIVENDI". Pintura en polvo de Adapta de Fermupe. Colour and Gloss according agreed previous projects
EFB-RS-581 | Surface preparation for steel shall be according to ISO 8501-3, level P2 or better, unless the corrosivity level requires P3 level preparation (e.g. for C4, high durability according to the ISO 12944 series of standards). | EFB-RS-581 | Surface preparation for steel shall be according to ISO 8501-3, level P2 or better, unless the corrosivity level requires P3 level preparation (e.g. for C4, high durability according to the ISO 12944 series of standards). | 100 | NA | HC_230303: Painted Al is considered | NA | HC_230303: Painted Al is considered
EFB-RS-582 | The edge preparation shall be sufficiently debarbed and/or rounded to ensure adherence. As a point of reference, the criteria given in the standard for steel (ISO 8501-3, level P2 or better) can be used. | EFB-RS-582 | The edge preparation shall be sufficiently debarbed and/or rounded to ensure adherence. As a point of reference, the criteria given in the standard for steel (ISO 8501-3, level P2 or better) can be used. | 100 | C | HC_230517: Painting system proposed and approved by CAF is: •“Sist. nº 2 Polvo. Fermupe: “Desengrase +desmutting Alumal Deox 445 + pasivado Alumal Bond 701 + acabado Adpata Color ADAPTA PES –RS Ó RM - gama VIVENDI". Pintura en polvo de Adapta de Fermupe. Colour and Gloss according agreed previous projects | C | HC_230517: Painting system proposed and approved by CAF is: •“Sist. nº 2 Polvo. Fermupe: “Desengrase +desmutting Alumal Deox 445 + pasivado Alumal Bond 701 + acabado Adpata Color ADAPTA PES –RS Ó RM - gama VIVENDI". Pintura en polvo de Adapta de Fermupe. Colour and Gloss according agreed previous projects
EFB-RS-583 | The equipment or component shall be painted using the color, gloss level and texture (if applicable) established by CAF for the corresponding project. | EFB-RS-583 | The equipment or component shall be painted using the color, gloss level and texture (if applicable) established by CAF for the corresponding project. | 100 | NC | HC_230517: Painting system proposed and approved by CAF is: •“Sist. nº 2 Polvo. Fermupe: “Desengrase +desmutting Alumal Deox 445 + pasivado Alumal Bond 701 + acabado Adpata Color ADAPTA PES –RS Ó RM - gama VIVENDI". Pintura en polvo de Adapta de Fermupe. Colour and Gloss according agreed previous projects The solution base proposed have been calculated taken into account the coulour and gloss agreed in previus project. I these parameter have to be defined during the development phase, if the colour, due to the customer's wishes, will vary, if there is a significant deviation in cost, it will be transferred to the cost of the equipment, both positively and negatively | NC | HC_230517: Painting system proposed and approved by CAF is: •“Sist. nº 2 Polvo. Fermupe: “Desengrase +desmutting Alumal Deox 445 + pasivado Alumal Bond 701 + acabado Adpata Color ADAPTA PES –RS Ó RM - gama VIVENDI". Pintura en polvo de Adapta de Fermupe. Colour and Gloss according agreed previous projects The solution base proposed have been calculated taken into account the coulour and gloss agreed in previus project. I these parameter have to be defined during the development phase, if the colour, due to the customer's wishes, will vary, if there is a significant deviation in cost, it will be transferred to the cost of the equipment, both positively and negatively
EFB-RS-584 | Non-painted edges that may be in contact with passengers, maintenance crew or operators shall not be sharp. To prove this, the standard ANSI/UL 1439 "Standard for safety. Tests for Sharpness of Edges on Equipment." may be used. | EFB-RS-584 | Non-painted edges that may be in contact with passengers, maintenance crew or operators shall not be sharp. To prove this, the standard ANSI/UL 1439 "Standard for safety. Tests for Sharpness of Edges on Equipment." may be used. | 100 | NA |  | NA
EFB-RS-587 | In case there is a degraded mode thermostat, the supplier must confirm the position of the thermostat in our supply and return duct. | EFB-RS-587 | In case there is a degraded mode thermostat, the supplier must confirm the position of the thermostat in our supply and return duct. | 100 | NA | HC_230517: Not thermostat mode is foreseen | NA | HC_230517: Not thermostat mode is foreseen
EFB-RS-588 | The covers of the HVAC equipment must have fixings both in the direction of movement of the train and in the perpendicular. | EFB-RS-588 | The covers of the HVAC equipment must have fixings both in the direction of movement of the train and in the perpendicular. | 100 | C |  | C
EFB-RS-589 | The supplier shall comply with the UNIFE database Railway Industry Substance List (RISL): • Substances classified as Prohibited, P(AR), shall not be present in the entire scope of supply. • Substances classified as Declarable for Assessment, D(FA), shall not be present in the scope of supply, unless assessment for use has been granted by the customer. • Substances classified as Declarable for Information, D(FI), shall be declared to the customer for their information. All substances that are not listed in UNIFE database and that are classified as “dangerous” according to the Regulation CLP, EC 1272/2008, shall be considered as D(FI). More information at http://www.unife-database.org The supplier shall provide a complete and signed declaration according to UNIFE template UNI-CR-001-02 ( http://unife.org/banners/81-material-declaration-template.html , Material Declaration and Substances Declaration, pink cells included) and the Railway Industry Substances List (RISL). | EFB-RS-589 | The supplier shall comply with the UNIFE database Railway Industry Substance List (RISL): • Substances classified as Prohibited, P(AR), shall not be present in the entire scope of supply. • Substances classified as Declarable for Assessment, D(FA), shall not be present in the scope of supply, unless assessment for use has been granted by the customer. • Substances classified as Declarable for Information, D(FI), shall be declared to the customer for their information. All substances that are not listed in UNIFE database and that are classified as “dangerous” according to the Regulation CLP, EC 1272/2008, shall be considered as D(FI). More information at http://www.unife-database.org The supplier shall provide a complete and signed declaration according to UNIFE template UNI-CR-001-02 ( http://unife.org/banners/81-material-declaration-template.html , Material Declaration and Substances Declaration, pink cells included) and the Railway Industry Substances List (RISL). | 100 | C |  | C
EFB-RS-590 | In case of the use of restricted substances included in RISL, it shall be delivered: - Safety Data Sheet in Spanish according to the 1907/2006 REACH. - Derogations/deviations | EFB-RS-590 | In case of the use of restricted substances included in RISL, it shall be delivered: - Safety Data Sheet in Spanish according to the 1907/2006 REACH. - Derogations/deviations | 100 | C |  | C
EFB-RS-591 | The supplier shall provide at Milestone 2 the product inventory of the system, with the list of items supplied and spare parts / materials used on its life cycle maintenance (included waste generated identified with WEC532/2000/EC), according to the “C.N4.94.502.00 CONTENT DECLARATION v7.1”. The template shall include the following information by each item supplied: • Item code • Item name • Material (pull-down menu) • Mass of the item (kg/train) • Recycled material content (%) • Item/Material origin (Country/City sent to CAF) | EFB-RS-591 | The supplier shall provide at Milestone 2 the product inventory of the system, with the list of items supplied and spare parts / materials used on its life cycle maintenance (included waste generated identified with WEC532/2000/EC), according to the “C.N4.94.502.00 CONTENT DECLARATION v7.1”. The template shall include the following information by each item supplied: • Item code • Item name • Material (pull-down menu) • Mass of the item (kg/train) • Recycled material content (%) • Item/Material origin (Country/City sent to CAF) | 100 | C |  | C
EFB-RS-592 | The Supplier shall provide a scrapping manual of the system/equipment. | EFB-RS-592 | The Supplier shall provide a scrapping manual of the system/equipment. | 100 | C | HC_230517: A special document to be quoted separately | C | HC_230517: A special document to be quoted separately
EFB-RS-593 | The scrapping manual shall include a detailed description of the element, for the purpose of facilitating dismantling and recycling at time of scrapping. The document shall include information on types of material (including type of plastic, type of metal), amounts, weights, European Waste Catalogue ("EWC") codes, hazardous components, chemical substances, etc. and where in the Train these are located. | EFB-RS-593 | The scrapping manual shall include a detailed description of the element, for the purpose of facilitating dismantling and recycling at time of scrapping. The document shall include information on types of material (including type of plastic, type of metal), amounts, weights, European Waste Catalogue ("EWC") codes, hazardous components, chemical substances, etc. and where in the Train these are located. | 100 | C | HC_230517: A special document to be quoted separately | C | HC_230517: A special document to be quoted separately
EFB-RS-595 | The equipment shall be designed and manufactured as to guarantee corrosion, oxidation, wear and ageing (radiation) protection throughout its design service life (40 years), according to the environment conditions described in this specification. CAF reserves the right to require documentation to prove compliance | EFB-RS-595 | The equipment shall be designed and manufactured as to guarantee corrosion, oxidation, wear and ageing (radiation) protection throughout its design service life (40 years), according to the environment conditions described in this specification. CAF reserves the right to require documentation to prove compliance | 100 | C |  | C
EFB-RS-596 | The supplier shall address corrosion protection in the design review process. | EFB-RS-596 | The supplier shall address corrosion protection in the design review process. | 100 | C |  | C
EFB-RS-597 | The supplier shall submit for CAF approval a "Corrosion control plan" that describes the methods employed to avoid corrosion of all metallic parts: Material selection, paint process, finishing process, sealing process, drainage, galvanic coupling of metals, corrosion inhibiting compounds, etc... | EFB-RS-597 | The supplier shall submit for CAF approval a "Corrosion control plan" that describes the methods employed to avoid corrosion of all metallic parts: Material selection, paint process, finishing process, sealing process, drainage, galvanic coupling of metals, corrosion inhibiting compounds, etc... | 100 | NC | HC_230517: Design according to the procedure already agreed with CAF for other projects. HC have an internal Technical instructions. | NC | HC_230517: Design according to the procedure already agreed with CAF for other projects. HC have an internal Technical instructions.
EFB-RS-598 | The supplier shall integrate the corrosion protection measurements, if any, into the maintenance manual: Access for maintenance, use of effective corrosion control programs in service, etc. | EFB-RS-598 | The supplier shall integrate the corrosion protection measurements, if any, into the maintenance manual: Access for maintenance, use of effective corrosion control programs in service, etc. | 100 | C |  | C
EFB-RS-599 | The equipment shall withstand the products that will be used for cleaning purposes such as acid soaps and diluted alkalise. CAF reserves the right to require tests to prove this. | EFB-RS-599 | The equipment shall withstand the products that will be used for cleaning purposes such as acid soaps and diluted alkalise. CAF reserves the right to require tests to prove this. | 100 | NC | HC_230517: Will depend of detergent Detergent list must be shared with HC | NC | HC_230517: Will depend of detergent Detergent list must be shared with HC
EFB-RS-600 | Metric threads according to ISO 68-1 (General basic threads – Basic profile – Part 1 Metric screw threads) shall be used in the vehicle. | EFB-RS-600 | Metric threads according to ISO 68-1 (General basic threads – Basic profile – Part 1 Metric screw threads) shall be used in the vehicle. | 100 | C |  | C
EFB-RS-601 | Supplier shall proposed the metric of the screw for equipment's fixation and his tightening torque. The final number of fixation and his metric shall be agreed between the supplier and CAF. | EFB-RS-601 | Supplier shall proposed the metric of the screw for equipment's fixation and his tightening torque. The final number of fixation and his metric shall be agreed between the supplier and CAF. | 100 | C |  | C
EFB-RS-602 | Fasteners and tightening torques shall comply with Technical Specification C.X1.97.030.01. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | EFB-RS-602 | Fasteners and tightening torques shall comply with Technical Specification C.X1.97.030.01. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | 100 | C |  | C
EFB-RS-603 | Fixing of the equipments to the train (roof, underframe, etc.) shall be done directly to the carbody rails or welded supports. | EFB-RS-603 | Fixing of the equipments to the train (roof, underframe, etc.) shall be done directly to the carbody rails or welded supports. | 100 | C |  | C
EFB-RS-604 | All equipment, mountings and fasteners of components shall withstand the forces and impacts as specified in EN 12663 without any part of the equipment becoming detached, and without any permanent deformation to the car-body. The category applicable in EN 12663 shall be defined in each project. If not, category P-II shall be fulfilled. A compliance certificate (with calculation proofs) must be provided by the supplier. | EFB-RS-604 | All equipment, mountings and fasteners of components shall withstand the forces and impacts as specified in EN 12663 without any part of the equipment becoming detached, and without any permanent deformation to the car-body. The category applicable in EN 12663 shall be defined in each project. If not, category P-II shall be fulfilled. A compliance certificate (with calculation proofs) must be provided by the supplier. | 100 | NA | HC_230517: EN 12663 Only apply for structural railway vehicle bodies. IEC 61373 is used. | NA | HC_230517: EN 12663 Only apply for structural railway vehicle bodies. IEC 61373 is used.
EFB-RS-605 | Suspension and fixing elements, if needed (vibration dampers, insulators etc.) will be included in the supplier’s scope of supply. The supplier will be responsible for the correct design of these elements. | EFB-RS-605 | Suspension and fixing elements, if needed (vibration dampers, insulators etc.) will be included in the supplier’s scope of supply. The supplier will be responsible for the correct design of these elements. | 100 | NC | HC_230517: Fixing elements are not under our scope of supply | NC | HC_230517: Fixing elements are not under our scope of supply
EFB-RS-606 | According to EN 45545-5:2013+A1:2015 (5.10), measures shall be taken to prevent the risk of fire in areas where heating equipment have a surface temperature of 200ºC or more under normal or fault operating conditions. The use of two separate levels of protective device, each capable of independently cutting off the energy supply to the heating equipment is mandatory. | EFB-RS-606 | According to EN 45545-5:2013+A1:2015 (5.10), measures shall be taken to prevent the risk of fire in areas where heating equipment have a surface temperature of 200ºC or more under normal or fault operating conditions. The use of two separate levels of protective device, each capable of independently cutting off the energy supply to the heating equipment is mandatory. | 100 | C |  | C
EFB-RS-607 | Equipment on the vehicle shall be marked with information about its function, a designation and reference to application documentation, to allow identification. The marking shall be permanent and resist detergent and graffiti removal agents. | EFB-RS-607 | Equipment on the vehicle shall be marked with information about its function, a designation and reference to application documentation, to allow identification. The marking shall be permanent and resist detergent and graffiti removal agents. | 100 | C |  | C
EFB-RS-608 | All controls and devices intended for customer personnel use shall be clearly labelled. | EFB-RS-608 | All controls and devices intended for customer personnel use shall be clearly labelled. | 100 | C |  | C
EFB-RS-609 | Labels and warning indicators shall be presented to CAF for approval. | EFB-RS-609 | Labels and warning indicators shall be presented to CAF for approval. | 100 | C |  | C
EFB-RS-610 | All equipment boxes shall be labelled with safety warnings for High Voltage if applicable. | EFB-RS-610 | All equipment boxes shall be labelled with safety warnings for High Voltage if applicable. | 100 | C |  | C
EFB-RS-611 | All equipment and devices shall be identified at least by their part number, hardware and software edition and serial number by means of stickers if the equipment is installed protected or by a metallic plate if the equipment is installed directly outside. | EFB-RS-611 | All equipment and devices shall be identified at least by their part number, hardware and software edition and serial number by means of stickers if the equipment is installed protected or by a metallic plate if the equipment is installed directly outside. | 100 | NC | HC_230517: Software edition is not included in the current identification plates, like all previous projects | NC | HC_230517: Software edition is not included in the current identification plates, like all previous projects
EFB-RS-612 | CAF code shall as well be included in the identification plate of each supply item. | EFB-RS-612 | CAF code shall as well be included in the identification plate of each supply item. | 100 | C |  | C
EFB-RS-613 | All numbering and marks of elements shall be clearly visible and not delectable. Codes shall be agreed with CAF. Text shall be in Spanish language. | EFB-RS-613 | All numbering and marks of elements shall be clearly visible and not delectable. Codes shall be agreed with CAF. Text shall be in Spanish language. | 100 | NC | HC_230517: Same aproach than RAMYA | NC | HC_230517: Same aproach than RAMYA
EFB-RS-614 | All pictograms related to safety (emergency handles/devices, evacuation doors, etc.) will be luminescent. | EFB-RS-614 | All pictograms related to safety (emergency handles/devices, evacuation doors, etc.) will be luminescent. | 100 | NA |  | NA
EFB-RS-615 | All machines (electrical equipment) shall carry a rating plate with the following information, as is appropriate to the equipment type: • serial number • manufacturer's type number • current, voltage and power ratings and whether continuous or otherwise • speed at rated current • maximum speed • field connection (series, separately excited, and so on) | EFB-RS-615 | All machines (electrical equipment) shall carry a rating plate with the following information, as is appropriate to the equipment type: • serial number • manufacturer's type number • current, voltage and power ratings and whether continuous or otherwise • speed at rated current • maximum speed • field connection (series, separately excited, and so on) | 100 | C |  | C
EFB-RS-616 | All labels, rating plates, and the arrows required for fans shall be mounted in such a position that they can be seen from the usual point of access. | EFB-RS-616 | All labels, rating plates, and the arrows required for fans shall be mounted in such a position that they can be seen from the usual point of access. | 100 | C |  | C
EFB-RS-617 | The labels shall be clearly stamped or engraved and securely attached to the machine. | EFB-RS-617 | The labels shall be clearly stamped or engraved and securely attached to the machine. | 100 | C |  | C
EFB-RS-618 | The mounting position for apparatus shall be labelled so that the position is clearly identified with or without the apparatus in place. | EFB-RS-618 | The mounting position for apparatus shall be labelled so that the position is clearly identified with or without the apparatus in place. | 100 | C |  | C
EFB-RS-619 | Underfloor and roof mounted equipment boxes shall be waterproof except where equipment must be ventilated. | EFB-RS-619 | Underfloor and roof mounted equipment boxes shall be waterproof except where equipment must be ventilated. | 100 | C |  | C
EFB-RS-620 | Underfloor and roof mounted equipment enclosures shall be watertight when subjected to high-pressure car wash, hose cleaning, and driving rain. | EFB-RS-620 | Underfloor and roof mounted equipment enclosures shall be watertight when subjected to high-pressure car wash, hose cleaning, and driving rain. | 100 | C |  | C
EFB-RS-621 | The size and weight of the cover shall permit removal and manipulation by one person. Orientative max values: -20kg for hinged doors -10kg for non-hinged doors | EFB-RS-621 | The size and weight of the cover shall permit removal and manipulation by one person. Orientative max values: -20kg for hinged doors -10kg for non-hinged doors | 100 | C |  | C
EFB-RS-622 | Air inlets/outlets and other external orifices on the equipments shall prevent ingress of water into 'dry' areas. | EFB-RS-622 | Air inlets/outlets and other external orifices on the equipments shall prevent ingress of water into 'dry' areas. | 100 | C |  | C
EFB-RS-623 | All systems, assemblies and controls shall be robust, of industrial quality, resist unauthorised use, physical abuse, vandalism and unauthorised removal. | EFB-RS-623 | All systems, assemblies and controls shall be robust, of industrial quality, resist unauthorised use, physical abuse, vandalism and unauthorised removal. | 100 | C |  | C
EFB-RS-624 | Covers that are hinged horizontally or vertically shall be provided with handles to ease opening operation. A retainer shall be either provided to hold the cover in open position | EFB-RS-624 | Covers that are hinged horizontally or vertically shall be provided with handles to ease opening operation. A retainer shall be either provided to hold the cover in open position | 100 | C |  | C
EFB-RS-625 | The lock and key for the enclosure of the components of the System shall be in accordance with CAF or Customer instructions. The equipment locks shall indicate in an unmistakable way the closed / opened position | EFB-RS-625 | The lock and key for the enclosure of the components of the System shall be in accordance with CAF or Customer instructions. The equipment locks shall indicate in an unmistakable way the closed / opened position | 100 | C |  | C
EFB-RS-626 | If needed the electrical enclosures will contain drain holes fitted with an approved draining mechanism for discharge of condensation | EFB-RS-626 | If needed the electrical enclosures will contain drain holes fitted with an approved draining mechanism for discharge of condensation | 100 | C |  | C
EFB-RS-627 | Type and opening direction of the access covers/doors must be agreed with CAF in design stage. | EFB-RS-627 | Type and opening direction of the access covers/doors must be agreed with CAF in design stage. | 100 | C |  | C
EFB-RS-628 | Covers shall be so designed that in the event of failure of a locking device in service, covers shall remain captured and shall not infringe the Kinematic Envelope. Otherwise, cover retention shall be provided to prevent covers from accidentally falling off (e.g. safety chain). | EFB-RS-628 | Covers shall be so designed that in the event of failure of a locking device in service, covers shall remain captured and shall not infringe the Kinematic Envelope. Otherwise, cover retention shall be provided to prevent covers from accidentally falling off (e.g. safety chain). | 100 | C |  | C
EFB-RS-629 | Doors of the boxes must allow total access to the components for their mounting and replacement compliant with the maintenability requirements included in the specifications. | EFB-RS-629 | Doors of the boxes must allow total access to the components for their mounting and replacement compliant with the maintenability requirements included in the specifications. | 100 | C |  | C
EFB-RS-630 | The system of covers’ attachment shall preserve the enclosure IP rating between train overhauls. | EFB-RS-630 | The system of covers’ attachment shall preserve the enclosure IP rating between train overhauls. | 100 | C |  | C
EFB-RS-631 | The cable glands, the electrical fittings or any other type of electrical conduction for the HV circuits that is to be handled by CAF when wiring the equipment interfaces shall be mounted on removable covers that in no case shall contain cables of another circuit type or connectors. | EFB-RS-631 | The cable glands, the electrical fittings or any other type of electrical conduction for the HV circuits that is to be handled by CAF when wiring the equipment interfaces shall be mounted on removable covers that in no case shall contain cables of another circuit type or connectors. | 100 | C |  | C
EFB-RS-632 | The cable glands, the electrical fittings or any other type of electrical conduction for the LV, SH or AC circuits that is to be be handled by CAF when wiring the equipment interfaces shall be mounted on removable covers that in no case shall contain cables of another circuit type or connectors. | EFB-RS-632 | The cable glands, the electrical fittings or any other type of electrical conduction for the LV, SH or AC circuits that is to be be handled by CAF when wiring the equipment interfaces shall be mounted on removable covers that in no case shall contain cables of another circuit type or connectors. | 100 | C |  | C
EFB-RS-633 | -The connection points of the electrical interfaces that require a tightening torque must be identified with the torque values in the drawing | EFB-RS-633 | -The connection points of the electrical interfaces that require a tightening torque must be identified with the torque values in the drawing | 100 | C |  | C
EFB-RS-634 | <Picture> | EFB-RS-634 | <Picture> | 100 | C |  | C
EFB-RS-640 | General review/overhaul shall take place at most every 15 years. | EFB-RS-640 | General review/overhaul shall take place at most every 15 years. | 100 | C |  | C
EFB-RS-641 | Visual inspection and cleaning of floor heaters shall be at most every 12 months and take less than 30minutes if performed by 2 people. | EFB-RS-641 | Visual inspection and cleaning of floor heaters shall be at most every 12 months and take less than 30minutes if performed by 2 people. | 100 | C | HC_230517: HC recommends a visual inspection every 12 months (seasonal components not working for a long time to be checked) | C | HC_230517: HC recommends a visual inspection every 12 months (seasonal components not working for a long time to be checked)
EFB-RS-642 | Checking of the correct functioning of floor heaters shall be performed at most every 12 months and take less than 5 minutes. | EFB-RS-642 | Checking of the correct functioning of floor heaters shall be performed at most every 12 months and take less than 5 minutes. | 100 | C |  | C
EFB-RS-643 | Assembly / disassembly of the HVAC equipment must take less than 1 hour by 2 people. | EFB-RS-643 | Assembly / disassembly of the HVAC equipment must take less than 1 hour by 2 people. | 100 | C | HC_230517: This is depending on depot instalation. | C | HC_230517: This is depending on depot instalation.
EFB-RS-644 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Replace air filters: at least 90 days. HVAC filter access shall be suitable to perform without the need of any special tool and by one person | EFB-RS-644 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Replace air filters: at least 90 days. HVAC filter access shall be suitable to perform without the need of any special tool and by one person | 100 | C | HC_230517: It will depend on several factors such us HVAC working hours and pollution in the air | C | HC_230517: It will depend on several factors such us HVAC working hours and pollution in the air
EFB-RS-645 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Detailed inspection: 1 year Detailed visual inspection of the cooling equipment, no leaks | EFB-RS-645 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Detailed inspection: 1 year Detailed visual inspection of the cooling equipment, no leaks | 100 | C |  | C
EFB-RS-646 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Clean 1 year Clean condenser, drains and evaporating | EFB-RS-646 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Clean 1 year Clean condenser, drains and evaporating | 100 | C |  | C
EFB-RS-647 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Detailed operation: 1 year Check detailed operation: check cooling mode operation, measure temperatures, refrigerant pressure and oil level. Include AUTOTEST option : The autotest is an internal development of supplier software the test all the functions of the HVAC unit. CAF send a digital signal to activate it and de software checks the following components: • Heating elements (no short-circuit), activating it. • High pressure switch in all the refrigerant circuits • Low pressure switch in all the refrigerant circuits • Bypass valve (if apply). The pressure transducer detects the change in the pressure when the bypass valve is activated. • Liquid valve (by pump down, if apply). • Air dampers (servomotors). • Compressors. Run it both circuits in order get a stabilization, at least 15 minutes. If any circuit is with low refrigerant level, it will be detected. Can be fist one circuit and then the second one, depending of the external conditions. | EFB-RS-647 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Detailed operation: 1 year Check detailed operation: check cooling mode operation, measure temperatures, refrigerant pressure and oil level. Include AUTOTEST option : The autotest is an internal development of supplier software the test all the functions of the HVAC unit. CAF send a digital signal to activate it and de software checks the following components: • Heating elements (no short-circuit), activating it. • High pressure switch in all the refrigerant circuits • Low pressure switch in all the refrigerant circuits • Bypass valve (if apply). The pressure transducer detects the change in the pressure when the bypass valve is activated. • Liquid valve (by pump down, if apply). • Air dampers (servomotors). • Compressors. Run it both circuits in order get a stabilization, at least 15 minutes. If any circuit is with low refrigerant level, it will be detected. Can be fist one circuit and then the second one, depending of the external conditions. | 100 | C | HC_230517: Specific mode defined fro this task | C | HC_230517: Specific mode defined fro this task
EFB-RS-648 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Overhaul 12.000 compresor working hours or 15 years | EFB-RS-648 | Maintenance Plan intervals must be equal or longer than the following: HVAC unit - Overhaul 12.000 compresor working hours or 15 years | 100 | C |  | C
EFB-RS-649 | The supplier must ensure that the fixing of the heating safety thermostats (Klixon) is robust, so that they cannot be misaligned either by themselves or by friction when accessing nearby maintenance items (e. g. during visual inspections and/or cleaning). | EFB-RS-649 | The supplier must ensure that the fixing of the heating safety thermostats (Klixon) is robust, so that they cannot be misaligned either by themselves or by friction when accessing nearby maintenance items (e. g. during visual inspections and/or cleaning). | 100 | C |  | C
EFB-RS-650 | The mechanical fixation of the heating safety thermostats (Klixon), cannot have slots, it must be fixed in position. | EFB-RS-650 | The mechanical fixation of the heating safety thermostats (Klixon), cannot have slots, it must be fixed in position. | 100 | C |  | C
EFB-RS-651 | The fixation of HVAC filters must be with quick fix/release locking system (if applicable) to avoid the use of tools to mount and dismount filters. | EFB-RS-651 | The fixation of HVAC filters must be with quick fix/release locking system (if applicable) to avoid the use of tools to mount and dismount filters. | 100 | C |  | C
EFB-RS-652 | The HVAC supplier must provide two alternatives filters concept solutions cartidge and filter mesh+frame. Both solutions must be interchangeable without any additional hardware. | EFB-RS-652 | The HVAC supplier must provide two alternatives filters concept solutions cartidge and filter mesh+frame. Both solutions must be interchangeable without any additional hardware. | 100 | NC | HC_230517: Cartridge filters considered in the initial offer | NC | HC_230517: Cartridge filters considered in the initial offer
EFB-RS-653 | The number of screw joints in the cooling circuit shall be minimized. The quantity of screwed joints shall be justified. | EFB-RS-653 | The number of screw joints in the cooling circuit shall be minimized. The quantity of screwed joints shall be justified. | 100 | C |  | C
EFB-RS-654 | Control panel accesible from inside the train including electronics with adequate ventilation.The supplier must include ventilation needs of their equipment | EFB-RS-654 | Control panel accesible from inside the train including electronics with adequate ventilation.The supplier must include ventilation needs of their equipment | 100 | C |  | C
EFB-RS-655 | Low and high pressure refrigeration circuit readings shall be monitored by pressure transducers and made available to TCMS. This readings from HVAC transducers shall be monitored by TCMS as part of the prognostics and diagnostics of the HVAC system. | EFB-RS-655 | Low and high pressure refrigeration circuit readings shall be monitored by pressure transducers and made available to TCMS. This readings from HVAC transducers shall be monitored by TCMS as part of the prognostics and diagnostics of the HVAC system. | 100 | C |  | C
EFB-RS-656 | The HVAC system will count, register and publish in the communication bus following information related to the condition base maintenance (CBM): - Compressor: number of starts - Compressors: working hours - Compresors comsuption: current - Condenser fan, supply air fain and exhaust air fan: working hours and number of starts. - Evaporator and condenser coils: Working refrigerant pressures. - Evaporator and condenser coils: Exit refigerant temperatures - CO2 Level - Dumpers: Position feedback. - General: Outside temperature, Return temperature, Impulsion temperature - Electrical protection: Number of cycles. - Contactors: number of starts/stops. - Filters: differential pressure. - air quality sensor - Valves: Number of cycles. - Compressor outlet pressure. (high pressure) - Compressor inlet pressures (low pressure) - Monitoring of safety chain thermostats - Monitor all the variables of the equipment control - Leak detection sensors The supplier should propose further parameters that could help to apply the CBM extensively. | EFB-RS-656 | The HVAC system will count, register and publish in the communication bus following information related to the condition base maintenance (CBM): - Compressor: number of starts - Compressors: working hours - Compresors comsuption: current - Condenser fan, supply air fain and exhaust air fan: working hours and number of starts. - Evaporator and condenser coils: Working refrigerant pressures. - Evaporator and condenser coils: Exit refigerant temperatures - CO2 Level - Dumpers: Position feedback. - General: Outside temperature, Return temperature, Impulsion temperature - Electrical protection: Number of cycles. - Contactors: number of starts/stops. - Filters: differential pressure. - air quality sensor - Valves: Number of cycles. - Compressor outlet pressure. (high pressure) - Compressor inlet pressures (low pressure) - Monitoring of safety chain thermostats - Monitor all the variables of the equipment control - Leak detection sensors The supplier should propose further parameters that could help to apply the CBM extensively. | 100 | NC | HC_2303517: Discusion aprobada en MD: - Compresors comsuption: current ==> Consumption meter are Not considered in the scope of supply proposed. - Evaporator and condenser coils: Exit refigerant temperatures ==> Refrigerant temperature sensor are not considered in the scope of supply proposed - Filters: differential pressure. ==> differential pressure are not considered in the scope of supply proposed - air quality sensor ==> ¿? - Leak detection sensors ==> Leak detection sensors are not considered in the scope of supply proposed CAF_21/3/23 The stimated / tabulated consumption of the compressor must be published. Related to the leakages detection, please use the same URBOS algorithm to detect gas leakages.The air quality sensor refers to CO2 sensor. CAF_230328: - HC revisa la posibilidad de publicar consumos tabulados. CAF propone publicar en función del estado. - Requiere sensorización, CAF revisa si existen compromisos con cliente. CAF concluye que no se requiere. - HC evalua como opción la incorporación del filtro. CAF revisa compromiso con cliente - El sensor de calidad del aire hace referencia al sensor de CO2, es necesario instalar este sensor. - No se requiere sensor de fuga, se registra a través de la no consecución del set durante un determinado periodo de tiempo. Puntos adicionales tratados en cabina que hacen referencia a sala: - HC no considera el número de ciclos para las válvulas de 4 vías. HC confirma que se puede considerar el nº de ciclos. HC_230417: - Ok, los consumos tabulados pueden ser definidos y acordados durante la fase de desarrollo del propyecto. una vez acordados pueden ser incluidos en la lista de variables a intercambiar. CAF_230426: Tenemos compromiso con cliente para el diferencial de presión de los filtros. HC debe confirmar. HC_230427: HC confirma que puede suministrar como opcional. | NC | HC_2303517: Discusion aprobada en MD: - Compresors comsuption: current ==> Consumption meter are Not considered in the scope of supply proposed. - Evaporator and condenser coils: Exit refigerant temperatures ==> Refrigerant temperature sensor are not considered in the scope of supply proposed - Filters: differential pressure. ==> differential pressure are not considered in the scope of supply proposed - air quality sensor ==> ¿? - Leak detection sensors ==> Leak detection sensors are not considered in the scope of supply proposed CAF_21/3/23 The stimated / tabulated consumption of the compressor must be published. Related to the leakages detection, please use the same URBOS algorithm to detect gas leakages.The air quality sensor refers to CO2 sensor. CAF_230328: - HC revisa la posibilidad de publicar consumos tabulados. CAF propone publicar en función del estado. - Requiere sensorización, CAF revisa si existen compromisos con cliente. CAF concluye que no se requiere. - HC evalua como opción la incorporación del filtro. CAF revisa compromiso con cliente - El sensor de calidad del aire hace referencia al sensor de CO2, es necesario instalar este sensor. - No se requiere sensor de fuga, se registra a través de la no consecución del set durante un determinado periodo de tiempo. Puntos adicionales tratados en cabina que hacen referencia a sala: - HC no considera el número de ciclos para las válvulas de 4 vías. HC confirma que se puede considerar el nº de ciclos. HC_230417: - Ok, los consumos tabulados pueden ser definidos y acordados durante la fase de desarrollo del propyecto. una vez acordados pueden ser incluidos en la lista de variables a intercambiar. CAF_230426: Tenemos compromiso con cliente para el diferencial de presión de los filtros. HC debe confirmar. HC_230427: HC confirma que puede suministrar como opcional.
EFB-RS-657 | All HVAC functional and maintenance checks shall be automated or mitigated by continuous monitoring of the unit performance. Only cleaning and filter changes should be left as manual tasks. | EFB-RS-657 | All HVAC functional and maintenance checks shall be automated or mitigated by continuous monitoring of the unit performance. Only cleaning and filter changes should be left as manual tasks. | 100 | C |  | C
EFB-RS-658 | The solar factor of the window shall be equal or less than 26 %. For thermal calculations of the HVAC system, consider 26%. | EFB-RS-658 | The solar factor of the window shall be equal or less than 26 %. For thermal calculations of the HVAC system, consider 26%. | 100 | C |  | C
EFB-RS-659 | All the WCs shall have an independent extraction system | EFB-RS-659 | All the WCs shall have an independent extraction system | 100 | NA | HC_230517: Extraction WC system not defined in this specification under HC scope of supply | NA | HC_230517: Extraction WC system not defined in this specification under HC scope of supply
EFB-RS-660 | The STD WC shall enable to mount a static resistance of 200 W on the ducting system | EFB-RS-660 | The STD WC shall enable to mount a static resistance of 200 W on the ducting system | 100 | NA |  | NA
EFB-RS-661 | The PMR WC shall enable to mount a static resistance of 200 W on the ducting system | EFB-RS-661 | The PMR WC shall enable to mount a static resistance of 200 W on the ducting system | 100 | NA |  | NA
EFB-RS-662 | The fan speed of the forced extraction system shall be able adjustable | EFB-RS-662 | The fan speed of the forced extraction system shall be able adjustable | 100 | C |  | C
EFB-RS-663 | Blocked forces transmitted by the saloon HVAC to the carbody structure for every operation condition of the equipment shall be evaluated by a direct method (using force cells) or by an indirect method (considering ISO 20270) | EFB-RS-663 | Blocked forces transmitted by the saloon HVAC to the carbody structure for every operation condition of the equipment shall be evaluated by a direct method (using force cells) or by an indirect method (considering ISO 20270) | 100 | C | HC_230517: The measurement will be direct metod. The unit will be place in a special frame on the floor and virbration measurement on the main bracket will be taken at diferent working conditions | C | HC_230517: The measurement will be direct metod. The unit will be place in a special frame on the floor and virbration measurement on the main bracket will be taken at diferent working conditions
EFB-RS-664 | The design of electrical wiring, cabling, connections, connectors, marking, etc., shall comply with EN 50343 (Railway applications – Rolling stock – Rules for installation of cabling). | EFB-RS-664 | The design of electrical wiring, cabling, connections, connectors, marking, etc., shall comply with EN 50343 (Railway applications – Rolling stock – Rules for installation of cabling). | 100 | C |  | C
EFB-RS-665 | The design of electrical wiring, cabling, connections, connectors, marking, etc., shall comply with EN 50343 regarding to protection against electrical hazard | EFB-RS-665 | The design of electrical wiring, cabling, connections, connectors, marking, etc., shall comply with EN 50343 regarding to protection against electrical hazard | 100 | C |  | C
EFB-RS-666 | The equipments will fulfil the rules for installation of cabling according to EN 50343 standard. | EFB-RS-666 | The equipments will fulfil the rules for installation of cabling according to EN 50343 standard. | 100 | C |  | C
EFB-RS-667 | The Technical Specification C.X1.97.022 defines the materials related to the type of product "flexible conduits" whose use has been approved by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | EFB-RS-667 | The Technical Specification C.X1.97.022 defines the materials related to the type of product "flexible conduits" whose use has been approved by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | 100 | NA | HC_230517: Same material and aproach than previus projects. NA, segun la defincion de la propia especificacion, aplica a los tubos intalados dentro del vehiculo y los instadaos fuera para (cita literal): - Cableado de elementos situados bajo bastidor desde la canalización principal - Conexiones de cables entre coches - Conexiones de cables entre caja y bogie Para el cableado interior del habitaculo, NA al HVAC por razones ovbias, y para los intalados fuera del vehiculo, ninguno de los tres casos se da en el HVAC, por lo tanto tambien NA.
EFB-RS-668 | Cable glands shall be mounted on a removable panel in order to ease the assembly and to avoid cutting terminal lugs for maintenance task such as removing the equipment. Cable glands shall also be chosen according to terminal lug dimensions (CAF definition) so that the cable with the terminal lug is able to pass through the body of the cable gland. | EFB-RS-668 | Cable glands shall be mounted on a removable panel in order to ease the assembly and to avoid cutting terminal lugs for maintenance task such as removing the equipment. Cable glands shall also be chosen according to terminal lug dimensions (CAF definition) so that the cable with the terminal lug is able to pass through the body of the cable gland. | 100 | C |  | C
EFB-RS-669 | All terminals will be screwed ring terminal type. | EFB-RS-669 | All terminals will be screwed ring terminal type. | 100 | C |  | C
EFB-RS-670 | All auxiliary contacts will guarantee more than 1 million cycles, oversized by 25% of the real load and made by recognized manufacturers | EFB-RS-670 | All auxiliary contacts will guarantee more than 1 million cycles, oversized by 25% of the real load and made by recognized manufacturers | 100 | C |  | C
EFB-RS-671 | Switches will have at least 2 contacts: normally open (NO), and normally closed (NC)) | EFB-RS-671 | Switches will have at least 2 contacts: normally open (NO), and normally closed (NC)) | 100 | C |  | C
EFB-RS-672 | Switches shall guarantee more than 1 million cycles (with 1A) and designed for operate permanently with up to 10 A. Wetting current shall be less than 50 mA (for the battery voltage) | EFB-RS-672 | Switches shall guarantee more than 1 million cycles (with 1A) and designed for operate permanently with up to 10 A. Wetting current shall be less than 50 mA (for the battery voltage) | 100 | C |  | C
EFB-RS-673 | The Technical Specification C.X1.97.025 defines the materials related to the type of product "Electrical terminals" whose use has been approved by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | EFB-RS-673 | The Technical Specification C.X1.97.025 defines the materials related to the type of product "Electrical terminals" whose use has been approved by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | 100 | NA | HC_230517: All the electrical material related to this project is railway material already used in all previous projects. NA, segun el alcance de la propia especificacion, "No es objeto de esta especificación el definir los terminales suministrados por los fabricantes de equipos y que sea necesario instalar en el tren para el correcto funcionamiento de dichos equipos". | NA | HC_230517: All the electrical material related to this project is railway material already used in all previous projects. NA, segun el alcance de la propia especificacion, "No es objeto de esta especificación el definir los terminales suministrados por los fabricantes de equipos y que sea necesario instalar en el tren para el correcto funcionamiento de dichos equipos".
EFB-RS-674 | The Technical Specification C.X1.97.023 defines the materials related to the type of product "Electrical Terminal Blocks" whose use has been approveed by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | EFB-RS-674 | The Technical Specification C.X1.97.023 defines the materials related to the type of product "Electrical Terminal Blocks" whose use has been approveed by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | 100 | NA | HC_230517: All the electrical material related to this project is railway material already used in all previous projects. NA, segun el alcance de la propia especificacion, "En esta especificación técnica no se incluyen las bornas que puedan suministrar los proveedores de los diferentes equipos y que sea necesario instalar en el tren para el correcto funcionamiento del equipo". | NA | HC_230517: All the electrical material related to this project is railway material already used in all previous projects. NA, segun el alcance de la propia especificacion, "En esta especificación técnica no se incluyen las bornas que puedan suministrar los proveedores de los diferentes equipos y que sea necesario instalar en el tren para el correcto funcionamiento del equipo".
EFB-RS-675 | Fibre optic and co-axial wiring shall be routed where possible such that the cables are not run in areas where movement is anticipated. | EFB-RS-675 | Fibre optic and co-axial wiring shall be routed where possible such that the cables are not run in areas where movement is anticipated. | 100 | C |  | C
EFB-RS-676 | The cables should fulfill one following standards, depending on the rated voltage, temperature, type (single core, multicore, shielded…) and any other installation requirement applicable to their specific use: - EN 50264-3-1 category “M” - EN50264-3-2 category “C” or higher - EN 50382 category “F” and 120ºC - EN 50306, category “M” (cables in protected areas, inside cabinets, etc.) | EFB-RS-676 | The cables should fulfill one following standards, depending on the rated voltage, temperature, type (single core, multicore, shielded…) and any other installation requirement applicable to their specific use: - EN 50264-3-1 category “M” - EN50264-3-2 category “C” or higher - EN 50382 category “F” and 120ºC - EN 50306, category “M” (cables in protected areas, inside cabinets, etc.) | 100 | C |  | C
EFB-RS-677 | If any special cable is needed for system connection, the supplier will specify it and will be in the supplier’s scope. Special cables are the ones that are not included in any of the categories listed in previous requirement | EFB-RS-677 | If any special cable is needed for system connection, the supplier will specify it and will be in the supplier’s scope. Special cables are the ones that are not included in any of the categories listed in previous requirement | 100 | C | HC_230517: Not foreseen at this stage | C | HC_230517: Not foreseen at this stage
EFB-RS-678 | The Technical Specification C.N4.97.086.01 defines the materials related to the type of product "Electrical cables" whose use has been approved by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | EFB-RS-678 | The Technical Specification C.N4.97.086.01 defines the materials related to the type of product "Electrical cables" whose use has been approved by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | 100 | C | HC_230517: All material offered is according to previus projects | C | HC_230517: All material offered is according to previus projects
EFB-RS-679 | Single-core cables connecting electrical components in different locations inside rolling stock vehicles shall have a nominal conductor cross-sectional area of at least 1,0mm2. For Unit Lines minimum admissible cable section will be 1.5 mm2 for single-core cables, and 2.5 mm² for Train lines for coupled operation. For multi-core cables the minimum allowed cross-sectional area will be 0,5mm2. For databus cables, such as Ethernet, smaller cross-sectional areas can be allowed. Although these requirements apply at train level, the Supplier shall take them into account for the equipment interface definition. | EFB-RS-679 | Single-core cables connecting electrical components in different locations inside rolling stock vehicles shall have a nominal conductor cross-sectional area of at least 1,0mm2. For Unit Lines minimum admissible cable section will be 1.5 mm2 for single-core cables, and 2.5 mm² for Train lines for coupled operation. For multi-core cables the minimum allowed cross-sectional area will be 0,5mm2. For databus cables, such as Ethernet, smaller cross-sectional areas can be allowed. Although these requirements apply at train level, the Supplier shall take them into account for the equipment interface definition. | 100 | C |  | C
EFB-RS-680 | All cables shall be labelled (method to be approved by CAF). | EFB-RS-680 | All cables shall be labelled (method to be approved by CAF). | 100 | C |  | C
EFB-RS-681 | The number of cable references to be fitted by CAF shall be minimized | EFB-RS-681 | The number of cable references to be fitted by CAF shall be minimized | 100 | C |  | C
EFB-RS-682 | The Technical Specification C.X1.97.026 defines the materials related to the type of product "Cable labels" whose use has been approved by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | EFB-RS-682 | The Technical Specification C.X1.97.026 defines the materials related to the type of product "Cable labels" whose use has been approved by CAF. If the supplier chooses another type of material not included in this TS, the supplier shall comply with the technical requirements defined for these materials and shall provide all the proofs necessary for their validation by the Customer. | 100 | C | HC_230517: All material offered is according to previus projects | C | HC_230517: All material offered is according to previus projects
EFB-RS-683 | Connectors shall be separated in four groups depending on the voltage level of the circuits or their EMC characteristics, in compliance with EN 50343. The following groups will be considered: High Voltage (HV), Alternating Current (AC), Direct Current (LV) and Signals (SH). These signals shall not be mixed between them. | EFB-RS-683 | Connectors shall be separated in four groups depending on the voltage level of the circuits or their EMC characteristics, in compliance with EN 50343. The following groups will be considered: High Voltage (HV), Alternating Current (AC), Direct Current (LV) and Signals (SH). These signals shall not be mixed between them. | 100 | C |  | C
EFB-RS-684 | All sockets and plugs shall be coded/ keyed to prevent misconnections, especially where connectors of the same type and form are in close proximity. Supplier shall provide coding details to both sockets and plugs. | EFB-RS-684 | All sockets and plugs shall be coded/ keyed to prevent misconnections, especially where connectors of the same type and form are in close proximity. Supplier shall provide coding details to both sockets and plugs. | 100 | C |  | C
EFB-RS-685 | Fixed part of all connectors shall be included in the supplier’s scope. | EFB-RS-685 | Fixed part of all connectors shall be included in the supplier’s scope. | 100 | C |  | C
EFB-RS-686 | Aereal parts of all connectors will be defined by the supplier. If proposed connectors are included within CAF standards (see next requirement for more detail), then they will be provided by CAF. Otherwise (not CAF standard connectors) they will be provided by the supplier. Preferred conectors are the ones described in CAF specification C.X1.97.024.01. | EFB-RS-686 | Aereal parts of all connectors will be defined by the supplier. If proposed connectors are included within CAF standards (see next requirement for more detail), then they will be provided by CAF. Otherwise (not CAF standard connectors) they will be provided by the supplier. Preferred conectors are the ones described in CAF specification C.X1.97.024.01. | 100 | C |  | C
EFB-RS-687 | Selected connectors and connector parts shall be chosen from: - Harting HAN, Sub-D and DIN 41612 type conectors included in the X.79.00999 CAF code table. - M12 connectors Harting or Phoenix Contact X.79.00252 CAF code table. These two tables include all connectors considered as CAF standards. In the scope of supply each of these parts must be codified with the correspondant CAF code (column "CODIGO CAF / CAF CODE"). Any exception to these codes, if necessary, must be agreed between CAF and the supplier. | EFB-RS-687 | Selected connectors and connector parts shall be chosen from: - Harting HAN, Sub-D and DIN 41612 type conectors included in the X.79.00999 CAF code table. - M12 connectors Harting or Phoenix Contact X.79.00252 CAF code table. These two tables include all connectors considered as CAF standards. In the scope of supply each of these parts must be codified with the correspondant CAF code (column "CODIGO CAF / CAF CODE"). Any exception to these codes, if necessary, must be agreed between CAF and the supplier. | 100 | C |  | C
EFB-RS-688 | CAF will consider positively those offers where the proposed connectors are within CAF standards, since those are the best option for CAF due to the experience in service, mounting skills, tools and purchasing and logistic optimisation. In case different connectors are proposed the supplier must explain the reasons behind this decision. | EFB-RS-688 | CAF will consider positively those offers where the proposed connectors are within CAF standards, since those are the best option for CAF due to the experience in service, mounting skills, tools and purchasing and logistic optimisation. In case different connectors are proposed the supplier must explain the reasons behind this decision. | 100 | C |  | C
EFB-RS-689 | In case of being part of supplier's scope (not CAF standard connectors) all pins which are of the same type will be delivered together in a single packet. A minimum of 10% extra pins quantity must be included. | EFB-RS-689 | In case of being part of supplier's scope (not CAF standard connectors) all pins which are of the same type will be delivered together in a single packet. A minimum of 10% extra pins quantity must be included. | 100 | NA | HC_230517: If CABL-RS-146 is NA,La conformidad de este requisito depende de la contestación de HC a CABL-RS-146 La cotestacion a CABL-RS-146 es NA. | NA | HC_230517: If CABL-RS-146 is NA,La conformidad de este requisito depende de la contestación de HC a CABL-RS-146 La cotestacion a CABL-RS-146 es NA.
EFB-RS-690 | All cable connectors and plug-in components including relays, printed circuit boards and electronic cards or racks shall comply with the following: • the plug or device shall be adequately and positively secured against working loose by means additional to the friction of the electrical contact • the plug contacts shall be adequately safeguarded against failure to make good contact • incorrect insertion of the plug or device shall be prevented by use of a guide, shield, or otherwise • where non-interchangeable parts have similar plug in components they shall be provided with a means to prevent them being inserted in the wrong position | EFB-RS-690 | All cable connectors and plug-in components including relays, printed circuit boards and electronic cards or racks shall comply with the following: • the plug or device shall be adequately and positively secured against working loose by means additional to the friction of the electrical contact • the plug contacts shall be adequately safeguarded against failure to make good contact • incorrect insertion of the plug or device shall be prevented by use of a guide, shield, or otherwise • where non-interchangeable parts have similar plug in components they shall be provided with a means to prevent them being inserted in the wrong position | 100 | C |  | C
EFB-RS-691 | All threads in the System will be metric (including, glands, fitting pipes etc.) | EFB-RS-691 | All threads in the System will be metric (including, glands, fitting pipes etc.) | 100 | C |  | C
EFB-RS-692 | All connectors, cable glands, fittings and accesories of the equipments must be adecuately protected when supplied. | EFB-RS-692 | All connectors, cable glands, fittings and accesories of the equipments must be adecuately protected when supplied. | 100 | C |  | C
EFB-RS-693 | The connectors shall have a locking system to ensure that the connector is fully mated. | EFB-RS-693 | The connectors shall have a locking system to ensure that the connector is fully mated. | 100 | C |  | C
EFB-RS-694 | The fixed end of any connector, which is normally unconnected (e.g. a test point), shall be sealed with a cover. | EFB-RS-694 | The fixed end of any connector, which is normally unconnected (e.g. a test point), shall be sealed with a cover. | 100 | C |  | C
EFB-RS-695 | All fibre optic and co-axial connectors shall be protected from all types of interference (physical, electrical and light) | EFB-RS-695 | All fibre optic and co-axial connectors shall be protected from all types of interference (physical, electrical and light) | 100 | C |  | C
EFB-RS-696 | High voltage connection screws, etc. will be provided by the system’s supplier. The details of all power connections (identification, metric, tightening torque, etc.) will be indicated in the mechanical drawings. | EFB-RS-696 | High voltage connection screws, etc. will be provided by the system’s supplier. The details of all power connections (identification, metric, tightening torque, etc.) will be indicated in the mechanical drawings. | 100 | C |  | C
EFB-RS-697 | The solar factor of the saloon and cabin door window shall be equal or less than 60 %. For thermal calculations of the HVAC system, consider 60%. | EFB-RS-697 | The solar factor of the saloon and cabin door window shall be equal or less than 60 %. For thermal calculations of the HVAC system, consider 60%. | 100 | NC | HC_230517: 26% Is considered. | NC | HC_230517: 26% Is considered.
EFB-RS-701 | Those points not expressly stated in this document conform to EN 14750-1 (category A vehicles). | EFB-RS-701 | Those points not expressly stated in this document conform to EN 14750-1 (category A vehicles). | 100 | C |  | C
EFB-RS-702 | Dampers shall be installed in the fresh air inlets of the HVAC equipment | EFB-RS-702 | Dampers shall be installed in the fresh air inlets of the HVAC equipment | 100 | C |  | C
EFB-RS-703 | Dampers shall activated before a tunnel entrance by the train control unit. This functionality will be defined during the project phase. | EFB-RS-707 | Dampers shall activated before a tunnel entrance by the train control unit. This functionality will be defined during the project phase. | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-704 | Dampers control strategy shall ensure dampers can be closed before entering a tunnel | EFB-RS-708 | Dampers control strategy shall ensure dampers can be closed before entering a tunnel | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-706 | Dampers shall be installed in the extraction | EFB-RS-706 | Dampers shall be installed in the extraction | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-707 | Dampers shall activated before a tunnel entrance by the train control unit. This functionality will be defined during the project phase. | EFB-RS-707 | Dampers shall activated before a tunnel entrance by the train control unit. This functionality will be defined during the project phase. | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-708 | Dampers control strategy shall ensure dampers can be closed before entering a tunnel | EFB-RS-708 | Dampers control strategy shall ensure dampers can be closed before entering a tunnel | 100 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-714 | El Tren propuesto está diseñado según las siguientes normas ambientales para garantizar el cumplimiento de los requisitos ambientales: | EFB-RS-714 | The proposed Train is designed according to the following environmental standards, in order to ensure compliance with environmental requirements: | 100 | C |  | C
EFB-RS-715 | - EN 50125-1 Aplicaciones ferroviarias. Condiciones ambientales para el equipo. Parte 1: Equipo a bordo del material rodante. | EFB-RS-715 | - EN 50125-1 Railway applications. Environmental conditions for equipment. Part 1: Equipment on board the rolling stock. | 100 | C | HC_230517: C understanding: A1: Altitude range relative to sea level: A1 (up to 1400 m above sea level). T3: Air temperatures: T3 (-25ºC to 45ºC) | C | HC_230517: C understanding: A1: Altitude range relative to sea level: A1 (up to 1400 m above sea level). T3: Air temperatures: T3 (-25ºC to 45ºC)
EFB-RS-716 | - EN 50155 Aplicaciones ferroviarias. Equipos electrónicos utilizados sobre material rodante. | EFB-RS-716 | - EN 50155 Railway applications. Electronic equipment used on rolling stock. | 100 | C |  | C
EFB-RS-717 | - EN 60529 Grados de proteccion | EFB-RS-717 | - EN 60529 Degrees of protection | 100 | C |  | C
EFB-RS-718 | Además, cada equipo cumple con otras normas específicas, que se identificarán en la descripción de cada equipo. El cumplimiento de estas normas y las condiciones de diseño apropiadas detalladas en las mismas darán como resultado que el equipo se diseñe específicamente para su entorno operativo previsto. | EFB-RS-718 | In addition, each piece of equipment complies with other specific standards, which shall be identified in the description of each piece of equipment. Compliance with these standards, and with the appropriate design conditions detailed therein, shall result in the equipment being designed specifically for its intended operating environment. | 100 | C |  | C
EFB-RS-719 | Los Trenes pueden circular en condiciones normales, bajo todas las condiciones climatológicas, ambientales y orográficas existentes en las líneas de ancho ibérico y ancho estándar de la RFIG, teniendo en cuenta que circulará en ambientes húmedos, salinos, secos, calurosos, etc. Los Trenes son capaces de operar sin ninguna restricción en sus prestaciones, a una altitud que puede variar desde el nivel del mar hasta 1.495 metros sobre el nivel del mar. | EFB-RS-719 | The Trains are able to run in standard conditions, under all existing weather, environmental, and orographic conditions, on the RFIG Iberian-gage and standard-gage lines, taking into account that they will run in humid, saline, dry, hot, and other environments. The Trains are capable of operating without any limitations on their performance at an altitude that may range from sea level to 1,495 m above sea level. | 100 | C |  | C
EFB-RS-720 | Los Trenes pueden circular en condiciones normales con temperaturas ambientales exteriores Clase T3 según la norma UNE EN 50125-1, comprendidas entre –25 ºC y +45 ºC. | EFB-RS-720 | The Trains are able to run in standard conditions at Class T3 ambient temperatures outside the vehicle as per the UNE-EN 50125-1 standard, ranging from -25ºC to +45ºC. | 100 | C |  | C
EFB-RS-721 | Todos los equipos electrónicos y los dispositivos de protección magnetotérmica son capaces de arrancar y funcionar con las temperaturas correspondientes a la Clase OT3, según lo indicado en la norma UNE EN 50155 relativa a equipos electrónicos. Con el fin de garantizar el cumplimiento de este requisito, se incorpora ventilación forzada en los armarios eléctricos que lo precisen. | EFB-RS-721 | All electronic equipment and thermo-magnetic protection devices are able to start and operate at temperatures corresponding to Class OT3, as indicated in the UNE-EN 50155 standard on electronic equipment. In order to ensure compliance with this requirement, forced ventilation is included in the electrical cabinets that require it. | 100 | C |  | C
EFB-RS-722 | Los Trenes están especialmente diseñados para funcionar de forma satisfactoria en caso de precipitaciones intensas, e impedir la entrada de agua, nieve, o cualquier tipo de polución, en el interior de sus equipos. | EFB-RS-722 | The Trains are specially designed to operate satisfactorily in the event of heavy rainfall and prevent any ingress of water, snow, or any type of pollution into their equipment. | 100 | C |  | C
EFB-RS-723 | En la concepción, diseño y construcción del Tren y de sus equipos, se ha tenido en cuenta la proteccion y estanqueidad de todos los equipos en cubierta y bajo bastidor, frente a la entrada de polen, polvo, agua o nieve. | EFB-RS-723 | The protection and watertightness of all the roof and underframe equipment against the ingress of pollen, dust, water, or snow has been taken into account during the conception, design, and construction of the Train and its equipment. | 100 | C |  | C
EFB-RS-724 | Una de las reglas generales del diseño es que la humedad no puede penetrar o condensarse en cualquier zona. Por lo que las soluciones de diseño evitan las zonas donde puede acumularse el agua, tanto en exterior como en el interior del vehículo y además proporcionan siempre una vía para garantizar la salida de esta agua al exterior. Para más información, referirse al apartado 3.7 “Condiciones técnicas de las cajas sin equipamiento interior” del presente DTT. | EFB-RS-724 | One of the general rules of the design is that moisture is not able to penetrate or condense in any area. Therefore, the design solutions avoid areas where water can accumulate, both outside and inside the rolling stock, and in addition, they always provide a channel to ensure that this water can be drained to the outside. For further information, refer to section 3.7 “Technical conditions for carbodies without interior equipment” of this TTD [Technical Train Document]. | 100 | C |  | C
EFB-RS-725 | Además de lo indicado en el párrafo anterior, se toman diferentes medidas para evitar la entrada de partículas sólidas y líquidos en el Tren y sus equipos. | EFB-RS-725 | In addition to that which is indicated in the previous paragraph, different measures are taken to prevent ingress of solid particles and liquids into the Train and its equipment. | 100 | C |  | C
EFB-RS-726 | El Tren se diseña para que en ningún caso se acumule el agua en aparatos o elementos montados bajo bastidor o en cubierta. | EFB-RS-726 | The Train is designed so that water will not, under any circumstances, accumulate in any of the apparatus or elements mounted underframe or on the roof. | 100 | C |  | C
EFB-RS-727 | Adicionalmente, los Trenes pueden arrancar y funcionar con unas temperaturas ambientales iniciales de -35ºC y de +50ºC. Cuando la temperatura ambiental sea de -35ºC o +50ºC, se realiza un arranque secuencial en el que primero arrancarán el TCMS, el Convertidor Auxiliar, y el HVAC. Estos equipos son capaces de arrancar en el rango de temperatura ambiental extendido entre -35ºC y +50ºC. Con estos equipos en funcionamiento, se acondiciona la temperatura interior del vehículo hasta -25ºC o +45ºC en función de la temperatura ambiental de inicio. Una vez acondicionada la temperatura interior, arrancan el resto de subsistemas del Tren. | EFB-RS-727 | Additionally, the Trains are able to start and operate at initial ambient temperatures of -35°C and of +50°C. When the ambient temperature is -35ºC or +50ºC, a sequential start-up is performed in which the TCMS, the Auxiliary Power Supply, and the HVAC will start first. This equipment is capable of starting up in the extended ambient temperature range between -35ºC and +50ºC. With this equipment in operation, the interior temperature of the rolling stock is conditioned to -25ºC or +45ºC, depending on the starting ambient temperature. Once the interior temperature has been conditioned, the rest of the Train’s subsystems will be started up. | 100 | C |  | C
EFB-RS-732 | All combustible materials shall comply with category HL2 of the EN45545-2 | EFB-RS-732 | All combustible materials shall comply with category HL2 of the EN45545-2 | 100 | C |  | C
EFB-RS-733 | Todos los sistemas indicados están integrados en los Trenes y están homologados para las condiciones ambientales especificadas en el presente documento. | EFB-RS-733 | All the above systems are integrated in the Trains, and are approved for the environmental conditions specified in this document. | 100 | C |  | C
EFB-RS-734 | For unrestricted access to the Spanish network under summer conditions, temperature zone T3 as specified in clause 4.2.6.1.1 shall be selected. | EFB-RS-734 | For unrestricted access to the Spanish network under summer conditions, temperature zone T3 as specified in clause 4.2.6.1.1 shall be selected. | 100 | C |  | C
EFB-RS-735 | (3) The temperature to consider for design purpose of rolling stock constituents shall take into account their integration in the rolling stock. | EFB-RS-735 | (3) The temperature to consider for design purpose of rolling stock constituents shall take into account their integration in the rolling stock. | 100 | C |  | C
EFB-RS-736 | (1) Rolling stock shall meet the requirements of this TSI when subject to snow, ice and hail conditions as defined in the specification referenced in Appendix J-1, index 35, which correspond to the nominal conditions (range). | EFB-RS-736 | (1) Rolling stock shall meet the requirements of this TSI when subject to snow, ice and hail conditions as defined in the specification referenced in Appendix J-1, index 35, which correspond to the nominal conditions (range). | 100 | C |  | C
EFB-RS-737 | (2) The effect of snow, ice and hail to consider for design purpose of rolling stock constituents shall take into account their integration in the rolling stock. | EFB-RS-737 | (2) The effect of snow, ice and hail to consider for design purpose of rolling stock constituents shall take into account their integration in the rolling stock. | 100 | C |  | C
EFB-RS-738 | (5) The selected range for “snow, ice and hail” (nominal or severe) and provision adopted shall be documented in the technical documentation described in clause 4.2.12.2 of this TSI. | EFB-RS-738 | (5) The selected range for “snow, ice and hail” (nominal or severe) and provision adopted shall be documented in the technical documentation described in clause 4.2.12.2 of this TSI. | 100 | C |  | C
EFB-RS-739 | All control logic softwares installed in the different systems of the train shall be unique and valid for all the different train tipologies (TEBMD - Tren Eléctrico Básico Media Distancia, and TEAMD - Tren Eléctrico Ampliado Media Distancia). In other words, the same SW shall be developed and uploaded in all the required Train typologies and shall work indistinctly. | EFB-RS-739 | All control logic softwares installed in the different systems of the train shall be unique and valid for all the different train tipologies (TEBMD - Tren Eléctrico Básico Media Distancia, and TEAMD - Tren Eléctrico Ampliado Media Distancia). In other words, the same SW shall be developed and uploaded in all the required Train typologies and shall work indistinctly. | 100 | C |  | C
EFB-RS-740 | All Software Licences and/or ICT systems that are required for the functionalities defined for this project, whether for on-board or shore-side equipment, shall be also part of the scope of the contract. | EFB-RS-740 | All Software Licences and/or ICT systems that are required for the functionalities defined for this project, whether for on-board or shore-side equipment, shall be also part of the scope of the contract. | 100 | NA | HC_230517: Licenses for general software are not included (Chrome, Firefox, etc). Maintenance software is and embbeded solution No licene is needed. | NA | HC_230517: Licenses for general software are not included (Chrome, Firefox, etc). Maintenance software is and embbeded solution No licene is needed.
EFB-RS-741 | All control logic sofwares installed in the different systems of the train shall be unique and valid throughout the train's life cycle. | EFB-RS-741 | All control logic sofwares installed in the different systems of the train shall be unique and valid throughout the train's life cycle. | 100 | C |  | C
EFB-RS-742 | Software for the electronic equipment shall be developed in accordance with EN 50128 Railway applications – Communication, signalling and processing systems – Software for railway control and protection systems. | EFB-RS-742 | Software for the electronic equipment shall be developed in accordance with EN 50128 Railway applications – Communication, signalling and processing systems – Software for railway control and protection systems. | 100 | C |  | C
EFB-RS-743 | Each supplier will submit to CAF a Software Requirements Specification. The supplier will inform CAF in case of the software (or part of it) is based in other project, specifying which part is new development and wich part is reused and if so from which project. | EFB-RS-743 | Each supplier will submit to CAF a Software Requirements Specification. The supplier will inform CAF in case of the software (or part of it) is based in other project, specifying which part is new development and wich part is reused and if so from which project. | 100 | C | HC_230517: Same software than in all previous projects. Specificaion already submitted, discussed and validated by CAF. ok and agree | C | HC_230517: Same software than in all previous projects. Specificaion already submitted, discussed and validated by CAF. ok and agree
EFB-RS-744 | Additionally the following software documentation is to be submitted (see due dates in "Suppliers General Non-Technical Requirements", documentation section ): Software Verification and Validation Plan, Software Design Description, Software Test Plan and Procedures and Software Requirements Traceabilty Matrix. | EFB-RS-744 | Additionally the following software documentation is to be submitted (see due dates in "Suppliers General Non-Technical Requirements", documentation section ): Software Verification and Validation Plan, Software Design Description, Software Test Plan and Procedures and Software Requirements Traceabilty Matrix. | 100 | C | HC_230517: Same software than in all previous projects. Specificaion already submitted, discussed and validated by CAF. ok and agree | C | HC_230517: Same software than in all previous projects. Specificaion already submitted, discussed and validated by CAF. ok and agree
EFB-RS-745 | The end-devices connected to the network will implement a DHCP client to get automatically the IP address, the subnet mask, the Gateway address and the DNS address. | EFB-RS-745 | The end-devices connected to the network will implement a DHCP client to get automatically the IP address, the subnet mask, the Gateway address and the DNS address. | 100 | C |  | C
EFB-RS-746 | All equipment connected to the Ethernet network shall send DHCP requests (DHCP DISCOVER/DHCP REQUEST) in the background until an IP address is received from the server (DHCP OFFER/DHCP ACK). | EFB-RS-746 | All equipment connected to the Ethernet network shall send DHCP requests (DHCP DISCOVER/DHCP REQUEST) in the background until an IP address is received from the server (DHCP OFFER/DHCP ACK). | 100 | C |  | C
EFB-RS-747 | If no IP address is obtained from the DHCP server in 120 seconds, the system will use a DEFAULT_ADDRESS to be defined during design stage. | EFB-RS-747 | If no IP address is obtained from the DHCP server in 120 seconds, the system will use a DEFAULT_ADDRESS to be defined during design stage. | 100 | C |  | C
EFB-RS-748 | In order to increase the number of ports of the network several end-devices might be connected to an unmanaged switch, which is finally connected to a managed switch. In this case DHCP option 82 is not enough to provide a unique IP address, therefore a CAF proprietary mechanism based on DHCP opt 224 must be implemented. There are two alternatives in order of preference: 1) Switches manage Option 224 locally. 2) One DHCP server implements the option 82 combined with 224. Switches act as relay agents. | EFB-RS-748 | In order to increase the number of ports of the network several end-devices might be connected to an unmanaged switch, which is finally connected to a managed switch. In this case DHCP option 82 is not enough to provide a unique IP address, therefore a CAF proprietary mechanism based on DHCP opt 224 must be implemented. There are two alternatives in order of preference: 1) Switches manage Option 224 locally. 2) One DHCP server implements the option 82 combined with 224. Switches act as relay agents. | 100 | C |  | C
EFB-RS-749 | End-devices connected to unmanaged switches will send a special code within the DHCP query option 224, derived from the RS485, CAN or MVB address and to be agreed during project phase. | EFB-RS-749 | End-devices connected to unmanaged switches will send a special code within the DHCP query option 224, derived from the RS485, CAN or MVB address and to be agreed during project phase. | 100 | C |  | C
EFB-RS-750 | No system shall use DNS names for service related functionality. In other words, the availability of the DNS server shall not lead any system to lose their functionality. If that is the case, the supplier shall propose design alternatives. | EFB-RS-750 | No system shall use DNS names for service related functionality. In other words, the availability of the DNS server shall not lead any system to lose their functionality. If that is the case, the supplier shall propose design alternatives. | 100 | C | HC_230517: DNS is not available in our electronic control | C | HC_230517: DNS is not available in our electronic control
EFB-RS-751 | The systems connected to the Ethernet network may implement DNS clients to allow communications based on alias, instead of based on IP addresses for maintenance purpose. The systems shall include a cache to allow communications between systems even the DNS server is not operating. Deviations from this requirement must be declared during offer phase so that CAF can check and eventually, validate them. | EFB-RS-751 | The systems connected to the Ethernet network may implement DNS clients to allow communications based on alias, instead of based on IP addresses for maintenance purpose. The systems shall include a cache to allow communications between systems even the DNS server is not operating. Deviations from this requirement must be declared during offer phase so that CAF can check and eventually, validate them. | 100 | C | HC_230517: DNS is not available in our electronic control | C | HC_230517: DNS is not available in our electronic control
EFB-RS-752 | No IGMP will be supported and only static multicast will be supported in the Ethernet network. | EFB-RS-752 | No IGMP will be supported and only static multicast will be supported in the Ethernet network. | 100 | C | HC_230517: Our electronic control is unicast | C | HC_230517: Our electronic control is unicast
EFB-RS-753 | Up to date configurable system parameters version, software versions, hardware serial numbers and hardware modification status for all Line Replaceable Unit (LRU) system components shall be made available to the Off-Train Systems. | EFB-RS-753 | Up to date configurable system parameters version, software versions, hardware serial numbers and hardware modification status for all Line Replaceable Unit (LRU) system components shall be made available to the Off-Train Systems. | 100 | C |  | C
EFB-RS-754 | All systems that are connected to the Train Control and Monitoring System (TCMS) and require time shall synchronize themselves with the clock of the TCMS. | EFB-RS-754 | All systems that are connected to the Train Control and Monitoring System (TCMS) and require time shall synchronize themselves with the clock of the TCMS. | 100 | C |  | C
EFB-RS-755 | The internal clocks of all (sub)systems shall run on UTC time. All times which are presented to the train staff and maintenance staff shall be presented in local time and shall automatically adapt to daylight saving time (DST). | EFB-RS-755 | The internal clocks of all (sub)systems shall run on UTC time. All times which are presented to the train staff and maintenance staff shall be presented in local time and shall automatically adapt to daylight saving time (DST). | 100 | C |  | C
EFB-RS-756 | Time synchronisation shall be done via TCMS bus communication or via Maintenance port Ethernet using NTP protocol with a synchronization of ±30 ms. | EFB-RS-756 | Time synchronisation shall be done via TCMS bus communication or via Maintenance port Ethernet using NTP protocol with a synchronization of ±30 ms. | 100 | C |  | C
EFB-RS-757 | Time stamp of datalog shall be equal or lower than 100 ms. | EFB-RS-757 | Time stamp of datalog shall be equal or lower than 100 ms. | 100 | C | HC_230517: The data logger is asynchronous type Si existe algún evento, el sistema lo registra | C | HC_230517: The data logger is asynchronous type Si existe algún evento, el sistema lo registra
EFB-RS-758 | Datalog can be stamp with additional datas from train information as: - Maitenance mode active - GPS coordinate sent by TCMS | EFB-RS-758 | Datalog can be stamp with additional datas from train information as: - Maitenance mode active - GPS coordinate sent by TCMS | 100 | C |  | C
EFB-RS-759 | Each sub-system must specify if any auto-test is realised and wicha are the times/conditions to be considered. | EFB-RS-759 | Each sub-system must specify if any auto-test is realised and wicha are the times/conditions to be considered. | 100 | C |  | C
EFB-RS-760 | The final ethernet addressing and requirements will be defined and agreed during design phase. | EFB-RS-760 | The final ethernet addressing and requirements will be defined and agreed during design phase. | 100 | C |  | C
EFB-RS-762 | If the equipment is connected to the Ethernet Comfort Network, the supplier shall fulfil CAF requirements defined in C.N4.98.108.30. | EFB-RS-762 | If the equipment is connected to the Ethernet Comfort Network, the supplier shall fulfil CAF requirements defined in C.N4.98.108.30. | 100 | C | HC_230517: A specific cbc of this document would be provide in the development project phase | C | HC_230517: A specific cbc of this document would be provide in the development project phase
EFB-RS-763 | Supplier must comply with the Communication Interface Specification document, which stablish the communication with train control Network (CIS) , code X.BK.F1500.00. This document will be handled to the supplier during offer stage. | EFB-RS-763 | Supplier must comply with the Communication Interface Specification document, which stablish the communication with train control Network (CIS) , code X.BK.F1500.00. This document will be handled to the supplier during offer stage. | 100 | C |  | C
EFB-RS-764 | Each specific train equipment / subsystem generally has its own processor and control logic, which is continuously communicating information to the train's general control and diagnosis system (TCMS), and which can manage and store all the variables necessary for its operations. functions and their maintenance. | EFB-RS-764 | Each specific train equipment / subsystem generally has its own processor and control logic, which is continuously communicating information to the train's general control and diagnosis system (TCMS), and which can manage and store all the variables necessary for its operations. functions and their maintenance. | 100 | C |  | C
EFB-RS-765 | During project phase, the supplier will deliver a document for each train equipment connected to the train network. These documents will be integrated in a general deliverable document of the project called "Architecture of the on-board networks and equipment on board", in which it shall be indicated by each system: . Basic function of the system. . Hardware description. . Firmware version. . SW version. . Operating systems. . Networks to which it is connected (TCN Network (Train Control Network), ETHERNET network). . Systems to which are directly conected. . Identification at the network. Identification of the network architecture scheme. . Analog/digital inputs. . Analog/digital outputs. . Configuration files/controls necessary to carry out its functions. . Files created for communication with other on-board equipment or ground level equipment. . SW for data extraction and /or configuration for equipment maintenance (deliver the SW program through a pen drive) | EFB-RS-765 | During project phase, the supplier will deliver a document for each train equipment connected to the train network. These documents will be integrated in a general deliverable document of the project called "Architecture of the on-board networks and equipment on board", in which it shall be indicated by each system: . Basic function of the system. . Hardware description. . Firmware version. . SW version. . Operating systems. . Networks to which it is connected (TCN Network (Train Control Network), ETHERNET network). . Systems to which are directly conected. . Identification at the network. Identification of the network architecture scheme. . Analog/digital inputs. . Analog/digital outputs. . Configuration files/controls necessary to carry out its functions. . Files created for communication with other on-board equipment or ground level equipment. . SW for data extraction and /or configuration for equipment maintenance (deliver the SW program through a pen drive) | 100 | C |  | C
EFB-RS-766 | Under no circumstance the Ethernet connection shall have the possibility to interfere/modify/affect the information of the other communication databuses (MVB, CAN, 485). | EFB-RS-766 | Under no circumstance the Ethernet connection shall have the possibility to interfere/modify/affect the information of the other communication databuses (MVB, CAN, 485). | 100 | C |  | C
EFB-RS-767 | In case the system provides serial communication (MVB, 485, CAN, Ethernet,..), communications tests will have to be performed at the communications system supplier to check the integrity of the communications, unless otherwise agreed. | EFB-RS-767 | In case the system provides serial communication (MVB, 485, CAN, Ethernet,..), communications tests will have to be performed at the communications system supplier to check the integrity of the communications, unless otherwise agreed. | 100 | C |  | C
EFB-RS-768 | The system will have a local port for diagnosis and maintenance purposes. This port shall permit real time monitoring, upgrading software, downloading history log and maintenance operations. The supplier shall defined the proposed type for this port at tender stage. | EFB-RS-768 | The system will have a local port for diagnosis and maintenance purposes. This port shall permit real time monitoring, upgrading software, downloading history log and maintenance operations. The supplier shall defined the proposed type for this port at tender stage. | 100 | C |  | C
EFB-RS-769 | The proposed system must be able to store a log file of the events occured in the last 72 hours, even in the absence of power supply. All storing functions, including logging, must be performed on a separated memory/disc partition or similar, in order to avoid in case of sudden shut-down any corruption of the main read only partition dedicated to the operating system or the main application. | EFB-RS-769 | The proposed system must be able to store a log file of the events occured in the last 72 hours, even in the absence of power supply. All storing functions, including logging, must be performed on a separated memory/disc partition or similar, in order to avoid in case of sudden shut-down any corruption of the main read only partition dedicated to the operating system or the main application. | 100 | C |  | C
EFB-RS-770 | Monitoring and diagnose software (for maintenance operations) must be provided (up to date operating system based), in Spanish language (to be confirmed with final customer). | EFB-RS-770 | Monitoring and diagnose software (for maintenance operations) must be provided (up to date operating system based), in Spanish language (to be confirmed with final customer). | 100 | NC | HC_230517: Software language is English. Same apprached approved in AMYA project. | NC | HC_230517: Software language is English. Same apprached approved in AMYA project.
EFB-RS-771 | All software tools shall be provided in the Spanish language. | EFB-RS-771 | All software tools shall be provided in the Spanish language. | 100 | NC | HC_230517: Software language is English. Same apprached approved in AMYA project. | NC | HC_230517: Software language is English. Same apprached approved in AMYA project.
EFB-RS-772 | The supplier must ensure (by means of certificate, written confirmation or similar) that the provided monitoring and diagnose software is appropriate and valid for the proposed system (because it is tested, validated, etc.), and that it is reliable to check the information of the system. This 'Pc Tools Validation Report' must be provided to CAF as requested in "Suppliers General Non-Technical Requirements", documentation section. | EFB-RS-772 | The supplier must ensure (by means of certificate, written confirmation or similar) that the provided monitoring and diagnose software is appropriate and valid for the proposed system (because it is tested, validated, etc.), and that it is reliable to check the information of the system. This 'Pc Tools Validation Report' must be provided to CAF as requested in "Suppliers General Non-Technical Requirements", documentation section. | 100 | C |  | C
EFB-RS-773 | All equipments must perform an autotest at start-up and inform CAF if any problem occurs. | EFB-RS-773 | All equipments must perform an autotest at start-up and inform CAF if any problem occurs. | 100 | C |  | C
EFB-RS-774 | If the diagnosis port is Ethernet based the following requirements are to be complied with. | EFB-RS-774 | If the diagnosis port is Ethernet based the following requirements are to be complied with. | 100 | C |  | C
EFB-RS-776 | The proposed system must be able to store a complete data log file that includes data such as local failure codes, digital/analogue data, performance counters, etc. The data log file can be extracted using a maintenance PC. | EFB-RS-776 | The proposed system must be able to store a complete data log file that includes data such as local failure codes, digital/analogue data, performance counters, etc. The data log file can be extracted using a maintenance PC. | 100 | C |  | C
EFB-RS-778 | The diagnosis software will be open and shall be enabled in any number o portable computers (and with different Windows versions) and be used simultaneously, without the need ig softeare or hardware keys. These keys will be explicitely rejected. | EFB-RS-778 | The diagnosis software will be open and shall be enabled in any number o portable computers (and with different Windows versions) and be used simultaneously, without the need ig softeare or hardware keys. These keys will be explicitely rejected. | 100 | C |  | C
EFB-RS-780 | Assemblies or components that are functionally interchangeable shall be physically interchangeable. Assemblies or components that are not functionally interchangeable shall not be physically interchangeable. | EFB-RS-780 | Assemblies or components that are functionally interchangeable shall be physically interchangeable. Assemblies or components that are not functionally interchangeable shall not be physically interchangeable. | 100 | C |  | C
EFB-RS-781 | Ensure the handling of LRUs weighing between 7 kg and 18 kg with two hands (this value can be adapted in function the customer). Not applicable for LRU that it can be successfully handled with one hand. | EFB-RS-781 | Ensure the handling of LRUs weighing between 7 kg and 18 kg with two hands (this value can be adapted in function the customer). Not applicable for LRU that it can be successfully handled with one hand. | 100 | C |  | C
EFB-RS-782 | Add guides or pins to facilitate the aligment of the fixation bolts , for suspended masses greater than 1 kg, and for supported masses greater than 18 kg | EFB-RS-782 | Add guides or pins to facilitate the aligment of the fixation bolts , for suspended masses greater than 1 kg, and for supported masses greater than 18 kg | 100 | C |  | C
EFB-RS-783 | All the non hexagonal bolt fixations of the equipement that require a maintenance task (or the access to) with a frequency of 1 year or less, shall be Torx type instead of allen, especially in metrics of 3 to 6 mm. | EFB-RS-783 | All the non hexagonal bolt fixations of the equipement that require a maintenance task (or the access to) with a frequency of 1 year or less, shall be Torx type instead of allen, especially in metrics of 3 to 6 mm. | 100 | NC | HC_230517: Not possible to be done in this phase. Normally preventive tasks like filter change are desigend to avoid the use of any tool. Covers lock to be defined and normally agree hexagonal bolts. Requirement to be check during project phase with a detailed design. The accessibility to Evaporator are is made by Quick Locks. Condenser Area has screws.The frecuency for Tasks in Condenser Area Similar to other projects. Tipically 1 or 2 years depending on the final intervals and km. Please check it,Hispacold complies with this requirement usuarlly. We will review together in design phase the compliance. Única zona limitante para el cumplimiento de este requisito es la tapa de la parte condensadora, que debrá ser métrica superior a la especificada. | NC | HC_230517: Not possible to be done in this phase. Normally preventive tasks like filter change are desigend to avoid the use of any tool. Covers lock to be defined and normally agree hexagonal bolts. Requirement to be check during project phase with a detailed design. The accessibility to Evaporator are is made by Quick Locks. Condenser Area has screws.The frecuency for Tasks in Condenser Area Similar to other projects. Tipically 1 or 2 years depending on the final intervals and km. Please check it,Hispacold complies with this requirement usuarlly. We will review together in design phase the compliance. Única zona limitante para el cumplimiento de este requisito es la tapa de la parte condensadora, que debrá ser métrica superior a la especificada.
EFB-RS-784 | Cover´s earthing wires: >When the entire cover (with or whithout handles) must be removed, the earthing wires should be on the outside. >On covers hinged the earthing wire should be inside | EFB-RS-784 | Cover´s earthing wires: >When the entire cover (with or whithout handles) must be removed, the earthing wires should be on the outside. >On covers hinged the earthing wire should be inside | 100 | C |  | C
EFB-RS-785 | Big or heavy covers shall include handles to ease mounting/dismounting process. | EFB-RS-785 | Big or heavy covers shall include handles to ease mounting/dismounting process. | 100 | C | HC_230517: Las tapas seran abisagradas, esto es suficiente para C de CAF, cambiado a C. | C | HC_230517: Las tapas seran abisagradas, esto es suficiente para C de CAF, cambiado a C.
EFB-RS-786 | Replacement of fan motor. Add solution to facilitate mounting and alignment of the fan. Guides, pins, support … Excluding resting horizontal position | EFB-RS-786 | Replacement of fan motor. Add solution to facilitate mounting and alignment of the fan. Guides, pins, support … Excluding resting horizontal position | 100 | C | HC_230517: Our motor fan does not need positioning or centering., the bracket provided for the evaporator fan allow this alignment. | C | HC_230517: Our motor fan does not need positioning or centering., the bracket provided for the evaporator fan allow this alignment.
EFB-RS-787 | System's design shall keep to a minimum the amount of special equipments and tools required to its succesful service. | EFB-RS-787 | System's design shall keep to a minimum the amount of special equipments and tools required to its succesful service. | 100 | C |  | C
EFB-RS-788 | Cable connectors shall be spaced far enough apart so that they can be grasped firmly for connecting and disconnecting. | EFB-RS-788 | Cable connectors shall be spaced far enough apart so that they can be grasped firmly for connecting and disconnecting. | 100 | C |  | C
EFB-RS-789 | Under frame and roof equipment: Multiple high voltage cables entrances through glands must be concentrated in a bolted cover. | EFB-RS-789 | Under frame and roof equipment: Multiple high voltage cables entrances through glands must be concentrated in a bolted cover. | 100 | NA |  | NA
EFB-RS-790 | The supplier must state all special tools and diagnostic software required for all preventive and corrective maintenance tasks . | EFB-RS-790 | The supplier must state all special tools and diagnostic software required for all preventive and corrective maintenance tasks . | 100 | C |  | C
EFB-RS-791 | External and interior connectors shall be properly identified and keyed so that they cannot be interchanged or improperly installed. Exceptions must be justified. | EFB-RS-791 | External and interior connectors shall be properly identified and keyed so that they cannot be interchanged or improperly installed. Exceptions must be justified. | 100 | C |  | C
EFB-RS-792 | Lifting aids: handles, lifting lugs, or approved functional equivalents shall be defined on heavy components (>15kg). These lifting aids shall be properly identified on the elements itself and stated in the maintenance documentation. | EFB-RS-792 | Lifting aids: handles, lifting lugs, or approved functional equivalents shall be defined on heavy components (>15kg). These lifting aids shall be properly identified on the elements itself and stated in the maintenance documentation. | 100 | C |  | C
EFB-RS-793 | The diagnosis software will be open and shall be enabled in any number of portable computers (and with different Windows versions) and be used simultaneously, without the need of software or hardware keys. These keys will be explicitely rejected. | EFB-RS-793 | The diagnosis software will be open and shall be enabled in any number of portable computers (and with different Windows versions) and be used simultaneously, without the need of software or hardware keys. These keys will be explicitely rejected. | 100 | C |  | C
EFB-RS-794 | All equipments that need checking lubricant level (gearboxes, compressors, engines, coolant circuits, etc. ...) will have a user-friendly sight glass or level display. | EFB-RS-794 | All equipments that need checking lubricant level (gearboxes, compressors, engines, coolant circuits, etc. ...) will have a user-friendly sight glass or level display. | 100 | NA | HC_230517: a checking lubricant level free compressor is provide. El compresor planteado no incorpora visor. | NA | HC_230517: a checking lubricant level free compressor is provide. El compresor planteado no incorpora visor.
EFB-RS-795 | Equipment installed on the roof shall have sufficient strength to withstand a 120 kg. person walking on top without permanent deformation or contact with underlying elements. If not possible the supplier shall justify the exceptions. | EFB-RS-795 | Equipment installed on the roof shall have sufficient strength to withstand a 120 kg. person walking on top without permanent deformation or contact with underlying elements. If not possible the supplier shall justify the exceptions. | 100 | C |  | C
EFB-RS-796 | The feasibility of disassembling entire assemblies for corrective or preventive maintenance must be ensured (eg: door mechanisms, cabin convectors, cabin pneumatic panels, ... etc ..) Describe or document the steps to follow to carry out its disassembly / assembly by milestone 2. Define special tools if necessary. | EFB-RS-796 | The feasibility of disassembling entire assemblies for corrective or preventive maintenance must be ensured (eg: door mechanisms, cabin convectors, cabin pneumatic panels, ... etc ..) Describe or document the steps to follow to carry out its disassembly / assembly by milestone 2. Define special tools if necessary. | 100 | C |  | C
EFB-RS-797 | The supplier will provide the following information: - Composition of the Maintenance Kits, including the codification of each spare part and its quantities within the kit as well as its description. - Reports required after a maintenance service or expertise detailing the actions carried out and the parts susceptible to change | EFB-RS-797 | The supplier will provide the following information: - Composition of the Maintenance Kits, including the codification of each spare part and its quantities within the kit as well as its description. - Reports required after a maintenance service or expertise detailing the actions carried out and the parts susceptible to change | 100 | C |  | C
EFB-RS-798 | The minimun order quantity for the spare parts will be coherent with the project needs. The supplier will provide this information within the LCC | EFB-RS-798 | The minimun order quantity for the spare parts will be coherent with the project needs. The supplier will provide this information within the LCC | 100 | C |  | C
EFB-RS-800 | The supplier must declare in offer stage its approach to Condition Based Maintenance (CBM), indicating for each part: · Expected Design Life; · Life Indicator (i.e aging, accumulation of cycles); · CBM Indicators (the variables that will be registered and transmitted to the bus); and · Limits/Conditions on which each registered variable shall be activated and the related logic for each Limit/Condition. CBM indicator management and the related logic will be done in CAF's monitoring system and not within each equipment, so that CAF is able to adjust the programming for Condition Based Maintenance as more experience in maintenance of these units/equipments is gathered." | EFB-RS-800 | The supplier must declare in offer stage its approach to Condition Based Maintenance (CBM), indicating for each part: · Expected Design Life; · Life Indicator (i.e aging, accumulation of cycles); · CBM Indicators (the variables that will be registered and transmitted to the bus); and · Limits/Conditions on which each registered variable shall be activated and the related logic for each Limit/Condition. CBM indicator management and the related logic will be done in CAF's monitoring system and not within each equipment, so that CAF is able to adjust the programming for Condition Based Maintenance as more experience in maintenance of these units/equipments is gathered." | 100 | C |  | C
EFB-RS-801 | (Optional) The system will count, register and publish in the communication bus following information related to the condition base maintenance (CBM): - Accumulated operating time of each electronic The supplier should propose further parameters that could help to apply the CBM extensively. | EFB-RS-801 | (Optional) The system will count, register and publish in the communication bus following information related to the condition base maintenance (CBM): - Accumulated operating time of each electronic The supplier should propose further parameters that could help to apply the CBM extensively. | 100 | NC | CAF_21/3/23 CAF will perform it internally | NC | CAF_21/3/23 CAF will perform it internally
EFB-RS-802 | The surface temperature of equipment or equipment enclosures (including heat convectors grille) in passenger, staff and luggage areas shall not exceed 60ºC under normal conditions; EN 45545-4:2013 (4.2.1) | EFB-RS-802 | The surface temperature of equipment or equipment enclosures (including heat convectors grille) in passenger, staff and luggage areas shall not exceed 60ºC under normal conditions; EN 45545-4:2013 (4.2.1) | 100 | C |  | C
EFB-RS-803 | The pneumatic connections and pipes shall be corrosion resistant, according to the expected environmental conditions in the operation. | EFB-RS-803 | The pneumatic connections and pipes shall be corrosion resistant, according to the expected environmental conditions in the operation. | 100 | NA |  | NA
EFB-RS-804 | The opening cover(s) of exterior equipment shall be fitted with more than one lock and it shall be possible to identify that the cover is not locked. | EFB-RS-804 | The opening cover(s) of exterior equipment shall be fitted with more than one lock and it shall be possible to identify that the cover is not locked. | 100 | C |  | C
EFB-RS-806 | The system and its components will require to have been gone through a hardening process to disable the unnecessary physical ports. A report will be provided. | EFB-RS-806 | The system and its components will require to have been gone through a hardening process to disable the unnecessary physical ports. A report will be provided. | 100 | C |  | C
EFB-RS-807 | The system and its components will require to have been gone through a hardening process to disable the unnecessary logical ports, services, protocols, users, etc. A report will be provided. | EFB-RS-807 | The system and its components will require to have been gone through a hardening process to disable the unnecessary logical ports, services, protocols, users, etc. A report will be provided. | 100 | C |  | C
EFB-RS-808 | The system and its components shall enforce identification (user) and authentication (password/key) in any management, configuration or diagnostic interface. | EFB-RS-808 | The system and its components shall enforce identification (user) and authentication (password/key) in any management, configuration or diagnostic interface. | 100 | C |  | C
EFB-RS-809 | The system and its components shall protect the locally stored passwords with strong cryptography. Implemented measures shall be explained and a report will be provided. | EFB-RS-809 | The system and its components shall protect the locally stored passwords with strong cryptography. Implemented measures shall be explained and a report will be provided. | 100 | C |  | C
EFB-RS-810 | The system and its components default passwords shall be changed. Selected password shall be agreed with CAF and changing procedure documented and provided on a report. | EFB-RS-810 | The system and its components default passwords shall be changed. Selected password shall be agreed with CAF and changing procedure documented and provided on a report. | 100 | C |  | C
EFB-RS-811 | The system and its components authentication mechanism shall allow to establish a strong password based on capital and lower case letters, non-alphanumeric characters (i.e. $, %, &, @, …) and a length of at least 8 characters. | EFB-RS-811 | The system and its components authentication mechanism shall allow to establish a strong password based on capital and lower case letters, non-alphanumeric characters (i.e. $, %, &, @, …) and a length of at least 8 characters. | 100 | C |  | C
EFB-RS-812 | The system shall enforce encrypted communications in any management, configuration or diagnostic interface. Unencrypted protocols such as Telnet or FTP, shall not be allowed. | EFB-RS-812 | The system shall enforce encrypted communications in any management, configuration or diagnostic interface. Unencrypted protocols such as Telnet or FTP, shall not be allowed. | 100 | NC | HC_230517: HISPACOLD sólo dispone de dos puertos para este fin que no incorporan cifrado: • Respecto al puerto USB del equipo, HISPACOLD confirma que se encuentra protegido físicamente sin fácil acceso al mismo ya que se utiliza para labores especiales, por lo que puede considerarse seguro. • Respecto al puerto Ethernet, HISPACOLD valorará como opción utilizar cifrado https en lugar de comunicación http. | NC | HC_230517: HISPACOLD sólo dispone de dos puertos para este fin que no incorporan cifrado: • Respecto al puerto USB del equipo, HISPACOLD confirma que se encuentra protegido físicamente sin fácil acceso al mismo ya que se utiliza para labores especiales, por lo que puede considerarse seguro. • Respecto al puerto Ethernet, HISPACOLD valorará como opción utilizar cifrado https en lugar de comunicación http.
EFB-RS-813 | The system and its components shall provide the capability to generate logs relevant to security of the following categories: login attempts. | EFB-RS-813 | The system and its components shall provide the capability to generate logs relevant to security of the following categories: login attempts. | 100 | C |  | C
EFB-RS-814 | The system and its components shall provide the capability to generate logs relevant to security of the following categories: configuration changes. | EFB-RS-814 | The system and its components shall provide the capability to generate logs relevant to security of the following categories: configuration changes. | 100 | C |  | C
EFB-RS-815 | The system and its components shall provide the capability to automatically and immediately transfer the generated logs to an external log management system (SIEM/SEM) using industry-best-practice protocols. | EFB-RS-815 | The system and its components shall provide the capability to automatically and immediately transfer the generated logs to an external log management system (SIEM/SEM) using industry-best-practice protocols. | 100 | NC | HC_230517: El registro de la intrusión es automático, pero el envío de este registro no es automático. Los eventos de intrusión si son posibles de automatizar su envío. Esta funcionalidad será definida en fase de proyecto acordada entre HC y CAF. CAF incorporará en sus protocolos de mantenimiento la necesidad de conectarse a la unidad para descargar el registro. La forma en la que el sistema informa de los logs será definida durante la etapa de proyecto. | NC | HC_230517: El registro de la intrusión es automático, pero el envío de este registro no es automático. Los eventos de intrusión si son posibles de automatizar su envío. Esta funcionalidad será definida en fase de proyecto acordada entre HC y CAF. CAF incorporará en sus protocolos de mantenimiento la necesidad de conectarse a la unidad para descargar el registro. La forma en la que el sistema informa de los logs será definida durante la etapa de proyecto.
EFB-RS-816 | The supplier of the system and its components shall propose a cyber security plan to ensure the cyber security of the system throughout its entire lifecycle. If the system is affected by a new vulnerability, the system supplier shall notify CAF and provide an appropriate security patch. | EFB-RS-816 | The supplier of the system and its components shall propose a cyber security plan to ensure the cyber security of the system throughout its entire lifecycle. If the system is affected by a new vulnerability, the system supplier shall notify CAF and provide an appropriate security patch. | 100 | C |  | C
EFB-RS-817 | The system and its components shall pass a penetration test and all the identified vulnerabilities shall be patched. | EFB-RS-817 | The system and its components shall pass a penetration test and all the identified vulnerabilities shall be patched. | 100 | C |  | C
EFB-RS-818 | The system shall automatically report any intrusion or anomaly to an external alert system. | EFB-RS-818 | The system shall automatically report any intrusion or anomaly to an external alert system. | 100 | NC | HC_230517: El registro de la intrusión es automático, pero el envío de este registro no es automático. Los eventos de intrusión si son posibles de automatizar su envío. Esta funcionalidad será definida en fase de proyecto acordada entre HC y CAF. CAF incorporará en sus protocolos de mantenimiento la necesidad de conectarse a la unidad para descargar el registro. La forma en la que el sistema informa de los logs será definida durante la etapa de proyecto. | NC | HC_230517: El registro de la intrusión es automático, pero el envío de este registro no es automático. Los eventos de intrusión si son posibles de automatizar su envío. Esta funcionalidad será definida en fase de proyecto acordada entre HC y CAF. CAF incorporará en sus protocolos de mantenimiento la necesidad de conectarse a la unidad para descargar el registro. La forma en la que el sistema informa de los logs será definida durante la etapa de proyecto.
EFB-RS-819 | HVAC Leakage problems. Establish specific vacum test during Origin Routine tests | EFB-RS-819 | HVAC Leakage problems. Establish specific vacum test during Origin Routine tests | 100 | C |  | C
EFB-RS-820 | HVAC Fresh air dampers: Include in Routine Tests Check that fresh air dampers have been correctly adjusted. | EFB-RS-820 | HVAC Fresh air dampers: Include in Routine Tests Check that fresh air dampers have been correctly adjusted. | 100 | C |  | C
EFB-RS-821 | Time synchronization Time synchronization of all on-board equipments (EVR, HMI, PPP) with an external time manager shall be done in accordance to the equipment specified in the CIS specifications (SAE, EVR, PPP by means of GPS, radio, NTP...). Verification of this point shall be included in the corresponding on-track type test procedures. | EFB-RS-821 | Time synchronization Time synchronization of all on-board equipments (EVR, HMI, PPP) with an external time manager shall be done in accordance to the equipment specified in the CIS specifications (SAE, EVR, PPP by means of GPS, radio, NTP...). Verification of this point shall be included in the corresponding on-track type test procedures. | 100 | C |  | C
EFB-RS-822 | - Auxiliary rotary machines: The part corresponding to the failure modes of the auxiliary rotating machinery of the priority equipment and their impact on the operation of the train is detailed in Annex 78 of the DTT (Train Technical Documentation) (B.2.11.2.O "RAMS summary tables"). | EFB-RS-822 | - Auxiliary rotary machines: The part corresponding to the failure modes of the auxiliary rotating machinery of the priority equipment and their impact on the operation of the train is detailed in Annex 78 of the TTD (Train Technical Documentation) (B.2.11.2.O "RAMS summary tables"). | 100 | NA |  | NA
EFB-RS-823 | (1) The quantity and quality of air provided inside the area of vehicles occupied by passengers and/or staff shall be such that no risk is developed to the health of passengers or staff additional to those resulting from the external ambient air quality. This is achieved by complying with the requirements set up below. A ventilation system shall maintain an acceptable interior CO 2 level under operational conditions. | EFB-RS-823 | (1) The quantity and quality of air provided inside the area of vehicles occupied by passengers and/or staff shall be such that no risk is developed to the health of passengers or staff additional to those resulting from the external ambient air quality. This is achieved by complying with the requirements set up below. A ventilation system shall maintain an acceptable interior CO 2 level under operational conditions. | 100 | C |  | C
EFB-RS-824 | (2) The CO 2 level shall not exceed 5 000 ppm in all operating conditions, excepted in the 2 cases below: — In case of interruption of the ventilation, due to an interruption of the main power supply or to a breakdown of the system, an emergency provision shall ensure the supply of outside air into all passenger and staff areas. If this emergency provision is ensured through battery supplied forced ventilation, the duration in which the CO 2 level will remain below 10 000 ppm shall be defined, assuming a passenger load derived from the load condition ‘design mass under normal payload’. The conformity assessment procedure is defined in clause 6.2.3.12. This duration shall not be less than 30 minutes. The duration shall be recorded in the technical documentation defined in clause 4.2.12 of this TSI. — In case of switch off or closing of all means of external ventilation, or switch off of air conditioning system, in order to prevent passengers being exposed to environmental fumes that may be present, especially in tunnels, and in the event of a fire, as described in clause 4.2.10.4.2. | EFB-RS-824 | (2) The CO 2 level shall not exceed 5 000 ppm in all operating conditions, excepted in the 2 cases below: — In case of interruption of the ventilation, due to an interruption of the main power supply or to a breakdown of the system, an emergency provision shall ensure the supply of outside air into all passenger and staff areas. If this emergency provision is ensured through battery supplied forced ventilation, the duration in which the CO 2 level will remain below 10 000 ppm shall be defined, assuming a passenger load derived from the load condition ‘design mass under normal payload’. The conformity assessment procedure is defined in clause 6.2.3.12. This duration shall not be less than 30 minutes. The duration shall be recorded in the technical documentation defined in clause 4.2.12 of this TSI. — In case of switch off or closing of all means of external ventilation, or switch off of air conditioning system, in order to prevent passengers being exposed to environmental fumes that may be present, especially in tunnels, and in the event of a fire, as described in clause 4.2.10.4.2. | 100 | C |  | C
EFB-RS-825 | (1) Conformity assessment of the CO 2 -levels is permitted to be established by calculation of fresh air ventilation volumes assuming an outside air quality containing 400 ppm CO 2 and an emission of 32 grams of CO 2 per passenger per hour. The number of passengers to be taken into account shall be derived from the occupation under the load condition ‘design mass under normal payload’, as stipulated in clause 4.2.2.10 of this TSI. | EFB-RS-825 | (1) Conformity assessment of the CO 2 -levels is permitted to be established by calculation of fresh air ventilation volumes assuming an outside air quality containing 400 ppm CO 2 and an emission of 32 grams of CO 2 per passenger per hour. The number of passengers to be taken into account shall be derived from the occupation under the load condition ‘design mass under normal payload’, as stipulated in clause 4.2.2.10 of this TSI. | 100 | C |  | C
EFB-RS-827 | The supplier shall confirm if heat pump functionallity could be in operation at the same time as the overhead heating stages of the HVAC system. | EFB-RS-827 | The supplier shall confirm if heat pump functionallity could be in operation at the same time as the overhead heating stages of the HVAC system. | 100 | C |  | C
EFB-RS-828 | Heat pump functionallity shall be capable to be in continuous operation at -5ºC external temperature. | EFB-RS-828 | Heat pump functionallity shall be capable to be in continuous operation at -5ºC external temperature. | 100 | NC | HC_230517: For performance issues, the limit of Heat pump mode is established in 2ºC | NC | HC_230517: For performance issues, the limit of Heat pump mode is established in 2ºC
EFB-RS-829 | The supplier shall confirm the heating power that could be achieved by the heat pump funtionallity at different external temperatures: - -5ºC - 0 ºC - 5 ºC - 10 ºC - 15 º | EFB-RS-829 | The supplier shall confirm the heating power that could be achieved by the heat pump funtionallity at different external temperatures: - -5ºC - 0 ºC - 5 ºC - 10 ºC - 15 º | 100 | C | HC_230517: For performance issues, the limit of Heat pump mode is established in 2ºC Would be for 2, 5, 10 and 15 ºC and 21ºC of interior temperature, the heating capacity would be aproximatelly: 2ºC==> 45,97Kw 5ºC==> 45,5 Kw 10ºC==> 44,84 Kw 15ºC==> 43,9 Kw | C | HC_230517: For performance issues, the limit of Heat pump mode is established in 2ºC Would be for 2, 5, 10 and 15 ºC and 21ºC of interior temperature, the heating capacity would be aproximatelly: 2ºC==> 45,97Kw 5ºC==> 45,5 Kw 10ºC==> 44,84 Kw 15ºC==> 43,9 Kw
EFB-RS-830 | Main train communication network is based on Ethernet communications. Bus connection type TCN (ECN) (ECN 61375-3-4) is required. | EFB-RS-830 | Main train communication network is based on Ethernet communications. Bus connection type TCN (ECN) (ECN 61375-3-4) is required. | 100 | C | HC_230517: TRDP or CAN have been proposed | C | HC_230517: TRDP or CAN have been proposed
EFB-RS-831 | In case other bus connection rather thatn Ethernet is proposed, other possibilities are: CAN RS485 Supplier shall indicate it at offer stage, and it shall be subject to approval by CAF. | EFB-RS-831 | In case other bus connection rather thatn Ethernet is proposed, other possibilities are: CAN RS485 Supplier shall indicate it at offer stage, and it shall be subject to approval by CAF. | 100 | C | HC_230517: TRDP or CAN have been proposed | C | HC_230517: TRDP or CAN have been proposed
EFB-RS-837 | - Estandarización: La concepción del vehículo trata de usar componentes y materiales estándares, tanto a nivel industrial como ferroviario, siempre y cuando se cumplan los requisitos citados en el Contrato. | EFB-RS-837 | - Standardization: The rolling stock design aims to use standard components and materials, at both an industrial and a railway level, as long as the requirements mentioned in the Contract are met. | 100 | C |  | C
EFB-RS-841 | La totalidad de cofres con elementos eléctricos/electrónicos, entendiendo por tales a aquellos habitáculos destinados a contener elementos que pueden operar encapsulados, tienen un grado de estanqueidad IP65. Para aquellos elementos que por su diseño / funcionalidad, requieren la circulación de aire exterior (tales como resistencias de freno, intercambiadores), o que precisen dar salida a gases, se considera válido con un grado de protección inferior. Todos estos casos se detallan en los próximos apartados. | EFB-RS-841 | All enclosures with electrical/electronic elements, understood as those enclosures intended to contain elements that can operate encapsulated, have an IP65 degree of watertightness. For those elements which, due to their design/functionality, require the circulation of external air (such as brake resistors, exchangers), or which require the exhaust of gases, a lower degree of protection is considered valid. All these cases are detailed in the following sections. | 100 | NC | HC_230517: The complete unit can not be rated with IP grade, because have some part open, so the equivalent for the electrical area inside of unit could be equivalent to IP X5. | NC | HC_230517: The complete unit can not be rated with IP grade, because have some part open, so the equivalent for the electrical area inside of unit could be equivalent to IP X5.
EFB-RS-847 | · CAF ha definido las variables que pueden ser monitorizadas en tiempo real, las cuales se adjuntan en el Anexo 48 del DTT (B.2.4.14.B “Listado inicial de variables a monitorizar”). | EFB-RS-847 | · CAF has defined the variables that can be monitored in real time, which are attached in Annex 48 of the TTD (Train Technical Documentation) (B.2.4.14.B "Initial list of variables to be monitored"). | 100 | C | HC_230517: Compresor: Número de arranques==> OK Compresor. Horas de operación==> OK Protección eléctrica: Número de ciclos==> OK Ventiladores: Horas de operación==> OK Contactores: número de arranques/paradas==> OK Filtros: diferencial de presión==> OK (on/off) Evaporador: Presión refrigerante==> OK Válvulas: Número de ciclos==> OK Temperatura interior del aire==> OK Temperatura del aire suministrado==> OK | C | HC_230517: Compresor: Número de arranques==> OK Compresor. Horas de operación==> OK Protección eléctrica: Número de ciclos==> OK Ventiladores: Horas de operación==> OK Contactores: número de arranques/paradas==> OK Filtros: diferencial de presión==> OK (on/off) Evaporador: Presión refrigerante==> OK Válvulas: Número de ciclos==> OK Temperatura interior del aire==> OK Temperatura del aire suministrado==> OK
EFB-RS-854 | The provider shall demonstrate that the systems are free of malware, vulnerabilities or weaknesses resulting from insecure development and/or testing processes. The successful tenderer shall establish a secure development and testing environment which shall: | EFB-RS-854 | The provider shall demonstrate that the systems are free of malware, vulnerabilities or weaknesses resulting from insecure development and/or testing processes. The successful tenderer shall establish a secure development and testing environment which shall: | 100 | C |  | C
EFB-RS-855 | Ensure that secure development and test environments (including development tools and facilities) are established for the development and testing of systems. | EFB-RS-855 | Ensure that secure development and test environments (including development tools and facilities) are established for the development and testing of systems. | 100 | C |  | C
EFB-RS-856 | Ensure that secure development and testing processes are established and applied to the development and testing of systems. | EFB-RS-856 | Ensure that secure development and testing processes are established and applied to the development and testing of systems. | 100 | C |  | C
EFB-RS-857 | Indicate the countries of origin of the products and where assembly, development and testing take place. | EFB-RS-857 | Indicate the countries of origin of the products and where assembly, development and testing take place. | 100 | C |  | C
EFB-RS-859 | The vendor must have a secure development methodology. | EFB-RS-859 | The vendor must have a secure development methodology. | 100 | C |  | C
EFB-RS-860 | The supplier must arrange, implement and supervise a secure development process that covers the entire cycle, from the use of the development methodology to testing in accordance with the requirements and principles of secure development. | EFB-RS-860 | The supplier must arrange, implement and supervise a secure development process that covers the entire cycle, from the use of the development methodology to testing in accordance with the requirements and principles of secure development. | 100 | C |  | C
EFB-RS-861 | Vendor will provide details of development practices and standards applied to the software, including the firmware used to ensure a high level of defense against unauthorized access. | EFB-RS-861 | Vendor will provide details of development practices and standards applied to the software, including the firmware used to ensure a high level of defense against unauthorized access. | 100 | C |  | C
EFB-RS-862 | Supplier shall provide documentation of coding practices used in the development of the delivered software. | EFB-RS-862 | Supplier shall provide documentation of coding practices used in the development of the delivered software. | 100 | C |  | C
EFB-RS-863 | Vendor shall provide documentation for input sanitization for all inputs, including, but not limited to, measures for the prevention of command injection, SQL injection, directory browsing, cross-site scripting, and buffer overflow. The system shall provide configurable and user-managed passwords for all interfaces. | EFB-RS-863 | Vendor shall provide documentation for input sanitization for all inputs, including, but not limited to, measures for the prevention of command injection, SQL injection, directory browsing, cross-site scripting, and buffer overflow. The system shall provide configurable and user-managed passwords for all interfaces. | 100 | C | HC_230517: II is a requirement refered to HTTP interfaces. It says that it is not allowed to introduce new code through the input interface C, it allow by HTTP but only thought signed files, "checksum". | C | HC_230517: II is a requirement refered to HTTP interfaces. It says that it is not allowed to introduce new code through the input interface C, it allow by HTTP but only thought signed files, "checksum".
EFB-RS-864 | The provider will provide a HIDS (Host Intrusion Detection System) configured on each information system. If the Operating System is owned by the manufacturer and cannot implement this security measure, it must identify those elements that cannot be protected by this type of control and the compensatory measures that it has designed and implemented. | EFB-RS-864 | The provider will provide a HIDS (Host Intrusion Detection System) configured on each information system. If the Operating System is owned by the manufacturer and cannot implement this security measure, it must identify those elements that cannot be protected by this type of control and the compensatory measures that it has designed and implemented. | 100 | C |  | C
EFB-RS-865 | The provider must configure the HIDS so that all system and user account connections are recorded. This log will be configured in such a way that an alarm can be sent to the TCMS (Train Control & Management System) if an abnormal situation (DoS or DDoS) occurs. | EFB-RS-865 | The provider must configure the HIDS so that all system and user account connections are recorded. This log will be configured in such a way that an alarm can be sent to the TCMS (Train Control & Management System) if an abnormal situation (DoS or DDoS) occurs. | 100 | NC | HC_230517: El registro de la intrusión es automático, pero el envío de este registro no es automático. Los eventos de intrusión si son posibles de automatizar su envío. Esta funcionalidad será definida en fase de proyecto acordada entre HC y CAF. CAF incorporará en sus protocolos de mantenimiento la necesidad de conectarse a la unidad para descargar el registro. La forma en la que el sistema informa de los logs será definida durante la etapa de proyecto. | NC | HC_230517: El registro de la intrusión es automático, pero el envío de este registro no es automático. Los eventos de intrusión si son posibles de automatizar su envío. Esta funcionalidad será definida en fase de proyecto acordada entre HC y CAF. CAF incorporará en sus protocolos de mantenimiento la necesidad de conectarse a la unidad para descargar el registro. La forma en la que el sistema informa de los logs será definida durante la etapa de proyecto.
EFB-RS-866 | The supplier will implement cryptographic systems to protect the confidentiality, integrity, authentication and non-repudiation of the devices and data streams. | EFB-RS-866 | The supplier will implement cryptographic systems to protect the confidentiality, integrity, authentication and non-repudiation of the devices and data streams. | 100 | C |  | C
EFB-RS-867 | The provider will apply application whitelisting technology that allows systems to run software only if it is included in such whitelisting and prevent the execution of any other unauthorized software. | EFB-RS-867 | The provider will apply application whitelisting technology that allows systems to run software only if it is included in such whitelisting and prevent the execution of any other unauthorized software. | 100 | NA | HC_230517:no application is needed to run our software or under our software | NA | HC_230517:no application is needed to run our software or under our software
EFB-RS-868 | The application's whitelisting technology should provide an alert when unauthorized software attempts to run. | EFB-RS-868 | The application's whitelisting technology should provide an alert when unauthorized software attempts to run. | 100 | NA | HC_230517:no application is needed to run our software or under our software | NA | HC_230517:no application is needed to run our software or under our software
EFB-RS-869 | It shall be possible to switch off ventilation when fire is detected. Fire detection indication is provided by a digital signal managed by CAF. The HVAC system shall turn ventilation off with a failure rate lower than 5E-07 1/h. If ventilation turn off is controlled by software, this software shall be certified EN50128:2011 SwSIL2. | EFB-RS-869 | It shall be possible to switch off ventilation when fire is detected. Fire detection indication is provided by a digital signal managed by CAF. The HVAC system shall turn ventilation off with a failure rate lower than 5E-07 1/h. If ventilation turn off is controlled by software, this software shall be certified EN50128:2011 SwSIL2. | 100 | C | HC_230517: Same approach than RAMYA is proposed, no controlled by software. This solution asure between 2E-07 to 3E-07 1/h according to manufacturer data sheet. | C | HC_230517: Same approach than RAMYA is proposed, no controlled by software. This solution asure between 2E-07 to 3E-07 1/h according to manufacturer data sheet.
EFB-RS-637 | The minimum Service Reliability MTBSF (Mean Time Between Service Failures) for the failure mode 'total loss of cooling capacity (excluding failures that lead to the loss of ventilation/heating) will be 222.717 hours/failure for each HVAC SALOON equipment, what is equivalent to MKBSF 9.768.289 km/failure (considering the following duty cycle: 35% for heating and 60% for cooling) | EFB-RS-850 | The minimum Service Reliability MTBSF (Mean Time Between Service Failures) for the failure mode 'total loss of cooling capacity (excluding failures that lead to the loss of ventilation/heating) will be 222.717 hours/failure for each HVAC SALOON equipment, what is equivalent to MKBSF 6.187.078 km/failure (considering the following duty cycle: 35% for heating and 60% for cooling) | 91.3846 | C | HC_230517: Calculated values provided in RAMS document | C | HC_230517: Calculated values provided in RAMS document
EFB-RS-638 | The minimum Service Reliability MTBSF (Mean Time Between Service Failures) for the failure mode 'total loss of heating capacity (excluding failures that lead to loss of ventilation/cooling)' will be 576.748 hours/failure for each HVAC SALOON equipment, what is equivalent to MKBSF 25.295.957 km/failure (considering the following duty cycle: 35% for heating and 60% for cooling) | EFB-RS-851 | The minimum Service Reliability MTBSF (Mean Time Between Service Failures) for the failure mode 'total loss of heating capacity (excluding failures that lead to loss of ventilation/cooling)' will be 576.748 hours/failure for each HVAC SALOON equipment, what is equivalent to MKBSF 16.022.059 km/failure (considering the following duty cycle: 35% for heating and 60% for cooling) | 91.3846 | C | HC_230517: Calculated values provided in RAMS document | C | HC_230517: Calculated values provided in RAMS document
EFB-RS-437 | The Supplier shall provide following details/calculations during the tender stage: 1) Considered fresh airflow and total air supply per car to guarantee CO2 concentration below 10.000 PPM inside the car after 60 minutes in emergency with EL4 (4p/m2) = 104 passengers per car. 2) Capacity required to the battery by the DC evaporator motor-fan | EFB-RS-914 | The Supplier shall provide following details/calculations during the tender stage: 1) Considered fresh airflow and total air supply per car to guarantee CO2 concentration below 10.000 PPM inside the car after 60 minutes in emergency with EL4 (4p/m2) = 143 passengers per car. 2) Capacity required to the battery by the DC evaporator motor-fan | 90.75 | C |  | C
EFB-RS-125 | The sound pressure level in a horizontal plane at the height of the saloon HVAC unit and 1 m away from the equipment surface (at the two lateral sides parallel to the train's sidewall) will not exceed the value of 73 dBA at any operating condition. This is applicable only if the previous requirement cannot be measured. | EFB-RS-843 | The sound pressure level in a horizontal plane at the height of the saloon HVAC unit and 1 m away from the equipment surface (at the two lateral sides parallel to the train's sidewall) will not exceed the value of 72 dBA at any operating condition. This is applicable only if the previous requirement cannot be measured. | 90 | NC | HC_230517: Mismos valores que en MD son esperados, 73 dB | NC | HC_230517: Mismos valores que en MD son esperados, 73 dB
EFB-RS-463 | When there is a fault in the one auxiliary power supply the saloon HVAC system will be receiving a degraded mode signal, and the HVAC system could be working at reduced performances. The reduction required shall depend on the capacity of the APS, and will confirm during a later design of the project. | EFB-RS-903 | When there is a fault in the one auxiliary power supply, the saloon HVAC system will be receiving a degraded mode signal, and the HVAC system could be working at reduced performances. The reduction required shall depend on the capacity of the APS, and will confirm during a later design of the project. | 90 | C |  | C
EFB-RS-636 | The minimum Service Reliability MTBSF (Mean Time Between Service Failures) for the failure mode 'total loss of ventilation capacity' will be 5.621.135 hours/failure for each HVAC SALOON equipment, what is equivalent to MKBSF 246.541.009 km/failure (considering the following duty cycle: 35% for heating and 60% for cooling) | EFB-RS-849 | The minimum Service Reliability MTBSF (Mean Time Between Service Failures) for the failure mode 'total loss of ventilation capacity' will be 5.621.135 hours/failure for each HVAC SALOON equipment, what is equivalent to MKBSF 156.155.130 km/failure (considering the following duty cycle: 35% for heating and 60% for cooling) | 90 | NC | HC_230517: Calculated values provided in RAMS document. el valor requerido es por equipo, por lo que solo depende del ventiladro de evaporador que esta al 100 %, si hacemos el calculo por coche, dos ventiladores, si que cumple. | NC | HC_230517: Calculated values provided in RAMS document. el valor requerido es por equipo, por lo que solo depende del ventiladro de evaporador que esta al 100 %, si hacemos el calculo por coche, dos ventiladores, si que cumple.
EFB-RS-531 | The required power demand has been calculated from the calculations under the above conditions. The installed capacity has been increased by 15% compared to all previous conditions (pre-cooling, pre-heating, heating and cooling). The most worst case car was taken into account. | EFB-RS-931 | The required power demand has been calculated from the calculations under the above conditions. The installed capacity has been increased by 15% compared to all previous conditions (pre-cooling, pre-heating, heating and cooling). The worst case car was taken into account. A2. As the units installed on the cars are identical, the other cars will benefit from a greater increase in installed power compared to this least advantageous car. | 89.1 | C |  | C
EFB-RS-635 | The Material Reliability includes all failures that request corrective maintenance. The minimum material reliability will be MTBF 30.933 h/failure for each HVAC SALOON, what is equivalent to MKBF 1.356.711 km/failure, considering the following duty cycle: 35% for heating and 60% for cooling | EFB-RS-848 | The Material Reliability includes all failures that request corrective maintenance. The minimum material reliability will be MTBF 30.933 h/failure for each HVAC SALOON, what is equivalent to MKBF 859.319 km/failure, considering the following duty cycle: 35% for heating and 60% for cooling | 89.1 | C | HC_230517: Calculated values provided in RAMS document | C | HC_230517: Calculated values provided in RAMS document
EFB-RS-124 | The sound pressure level in a horizontal plane at the height of the saloon HVAC unit and 7.5 m away from its center (at the two lateral sides parallel to the train's sidewall) will not exceed the value of 64 dBA at any operating condition. | EFB-RS-842 | The sound pressure level in a horizontal plane at the height of the saloon HVAC unit and 7.5 m away from its center (at the two lateral sides parallel to the train's sidewall) will not exceed the value of 63 dBA at any operating condition. | 88 | NC | HC_230517: Mismos valores que en MD son esperados, 64 dB | NC | HC_230517: Mismos valores que en MD son esperados, 64 dB
EFB-RS-362 | The evaporator shall be constructed of copper tubes with mechanically crimped aluminium fins. The Supplier will confirm during the tender stage if there shall be fitted a double evaporator coil per evaporator section or 2 single evaporator coils per evaporator section. | EFB-RS-920 | The evaporator shall be constructed of copper tubes with mechanically crimped aluminium fins. The Supplier will confirm during the tender stage if there shall be fitted a single evaporator coil per evaporator section, double evaporator coil per evaporator section or 2 single evaporator coils per evaporator section. | 88 | C | HC_230517: a single evaporator coil per evaporator section is considered | C | HC_230517: a single evaporator coil per evaporator section is considered
EFB-RS-525 | - intake of outside air in the condition corresponding to the "normal mode" laid out in the following section (at 40°C outside this corresponds to 15 m3/h per passenger, considering the total seating capacity offered). | EFB-RS-929 | - intake of outside air in the condition corresponding to the "normal mode" laid out in the following section (at 40°C outside this corresponds to 15 m3/h per passenger, considering the total seating capacity offered and two people per square meter in standing areas). | 86.625 | C |  | C
EFB-RS-529 | - intake of outside air in the condition corresponding to the "normal mode" laid out in the following section (at -10°C outside this corresponds to 10 m3/h per passenger, considering the total seating capacity offered). | EFB-RS-930 | - intake of outside air in the condition corresponding to the "normal mode" laid out in the following section (at -10°C outside this corresponds to 10 m3/h per passenger, considering the total seating capacity offered and 2 people per square meter in standing areas). | 86.625 | C |  | C
EFB-RS-135 | The Sound Power Level on the air return openning (including the exhaust) of the saloon HVAC will not exceed the value of 65 dBA (per evaporator unit). | EFB-RS-846 | The Sound Power Level on the air return openning (including the exhaust) of the saloon HVAC will not exceed the value of 62 dBA (per evaporator unit). | 82.5 | NC | HC_230517: Mismos valores que en MD son esperados, 65 dB | NC | HC_230517: Mismos valores que en MD son esperados, 65 dB
EFB-RS-156 | Saloon HVAC unit shall withstand the following pressure drops while providing the operational performance required by the [EN14750]: - Saloon HVAC. Supply duct pressure drop of 115 Pa @ 4500 m3/h - Saloon HVAC. Return duct pressure drop of 100 Pa @ 3600 m3/h - Saloon HVAC. Overpressure of 50Pa | EFB-RS-157 | Saloon HVAC unit shall withstand the following pressure drops while providing the operational performance required by the [EN14750]: - Saloon HVAC. Supply duct pressure drop of 150 Pa @ 5200 m3/h - Saloon HVAC. Return duct pressure drop of 100 Pa @ 3600 m3/h - Saloon HVAC. Overpressure of 50Pa | 79.2 | C |  | C
EFB-RS-729 | The maximum weight of each saloon HVAC equipment will be 585 kg including all necessary components to perform the intended function | EFB-RS-933 | The maximum weight of each saloon HVAC equipment will be 400 kg including all necessary components to perform the intended function | 79.2 | C |  | C
EFB-RS-639 | The minimum Service Reliability MTBSF (Mean Time Between Service Failures) for the failure mode 'total loss of heating or cooling capacity (excluding failures that lead to loss of ventilation and considering only the common failures that lead to both)' will be 2.538.819 hours/failure for each HVAC SALOON equipment, what is equivalent to MKBSF 111.351.711 km/failure (considering the following duty cycle: 35% for heating and 60% for cooling) | EFB-RS-852 | The minimum Service Reliability MTBSF (Mean Time Between Service Failures) for the failure mode 'total loss of heating or cooling capacity (excluding failures that lead to loss of ventilation and considering only the common failures that lead to both)' will be 5.191.070 hours/failure for each HVAC SALOON equipment, what is equivalent to MKBSF 144.207.925 km/failure (considering the following duty cycle: 35% for heating and 60% for cooling) | 79.2 | C | HC_230517: Calculated values provided in RAMS document | C | HC_230517: Calculated values provided in RAMS document
EFB-RS-133 | The Sound Power Level on the exterior surface of the saloon HVAC will not exceed the value of 90 dBA. | EFB-RS-844 | The Sound Power Level on the exterior surface of the saloon HVAC will not exceed the value of 89 dBA. | 74.25 | NC | HC_230517: Mismos valores que en MD son esperados, 90 dB | NC | HC_230517: Mismos valores que en MD son esperados, 90 dB
EFB-RS-134 | The Sound Power Level on the air supply of the saloon HVAC will not exceed the value of 81 dBA (per evaporator unit). | EFB-RS-845 | The Sound Power Level on the air supply of the saloon HVAC will not exceed the value of 78 dBA (per evaporator unit). | 74.25 | NC | HC_230517: 80 dB son esperados. | NC | HC_230517: 80 dB son esperados.
EFB-RS-199 | The proposed solution shall be suitable for the operation up to the design speed of the train (200 Km/h). | EFB-RS-898 | The proposed solution shall be suitable for the operation up to the design speed of the train (180 Km/h). | 74.25 | C |  | C
EFB-RS-342 | The maximum fresh airflow of the equipment shall be 25 m3/h per passenger considering seated passengers. | EFB-RS-906 | The maximum fresh airflow of the equipment shall be 25 m3/h per passenger considering seated passengers + 2p/m2. | 74.25 | C |  | C
EFB-RS-779 | The Material Reliability includes all failures that request corrective maintenance. The minimum material reliability will be MTBF 220.000 h/failure for each air heater (convector), what is equivalent to MKBF 9.649.123 km/failure | EFB-RS-832 | The Material Reliability includes all failures that request corrective maintenance. The minimum material reliability will be MTBF 220.000 h/failure for each air heater (convector), what is equivalent to MKBF 6.111.600 km/failure | 74.25 | C | HC_230517: Calculated values provided in RAMS document | C | HC_230517: Calculated values provided in RAMS document
EFB-RS-229 | The HVAC proposed shall be designed for the most demanding car in terms of thermal demand according with all conditions defined in Section 3.1 (Cooling, Heating, Precooling, Preheating) and considering 15% spare capacity. The cooling performance to be proposed shall be the most demending according to cases 1,2, 12, 13, 14 of the sheet 'Calculations to perform SALOON' and considering 15% spare capacity. The heating performance to be proposed shall be the most demending according to cases 16, 17, 29, 30, 31 of the sheet 'Calculations to perform SALOON' and considering 15% spare capacity. The cars to be analyzed are: - Cabin car A2: 39 seated passengers - Intermediate B1: 60 seated passengers The dimensions and main characteristics of both cars are included in sheet 'Vehicle Parameters'. | EFB-RS-900 | The HVAC proposed shall be designed for the most demanding car in terms of thermal demand according with all conditions defined in Section 3.1 (Cooling, Heating, Precooling, Preheating) and considering 15% spare capacity. The cooling performance to be proposed shall be the most demending according to cases 1 & 11 of the sheet 'Calculations to perform SALOON' and considering 15% spare capacity. The heating performance to be proposed shall be the most demending according to cases 14 & 26 of the sheet 'Calculations to perform SALOON' and considering 15% spare capacity. The car to be analyzed is: - Cabin car A2: 68 seated passengers + 2 p/m2. Total of 105 passengers The dimensions and main characteristics of both cars are included in sheet 'Vehicle Parameters'. | 73.3333 | C |  | C
EFB-RS-713 | The maximum dimensions of the convectors to be proposed shall be as follows: - Underseat floor convectors (L:332 x W:200 x H:230 mm) - Platform converctors (L:410 x W:170 x H:194 mm) | EFB-RS-912 | The maximum dimensions of the convectors to be proposed shall be as follows: - Underseat floor convectors (L:332 x W:200 x H:230 mm) - Tip up convectors (L:400 x W:228 x H:100 mm) | 70.7143 | C | HC_230517: en principio los Tip up que se han planteado para CER están basados en 9422273/9600003 de AMYA. | C | HC_230517: en principio los Tip up que se han planteado para CER están basados en 9422273/9600003 de AMYA.
EFB-RS-195 | The Scope of Supply of the System will include at least following components per car, that will be described in more detail in each section of this specification: - One EC compact HVAC unit per car including each of them: - 2 reversable cooling circuits. Approximated cooling power 41 kW at 40ºC 43%RH, to be justified by thermal calculations. Heating power 40 kW at -10ºC outside and 22ºC inside. - air filters - temperature sensors, thermostats, pressure gauges, pressure switches... - double sealing barrier in the interface with the carbody structure to avoid any water getting into the saloon area. - electrical connectors - 1 electric control panel including the protections and control components for the HVAC unit, including the electronic controller equipped with Ethernet port. - Exhaust system inside the HVAC unit - temperature sensors to be installed outside the HVAC unit, in case they are required -OPTION 1: CO2 detector to regulate the fresh airflow -OPTION 2: Floor Heat convectors. Approximated total floor heating power 11 kW: (6 x 1,5 kW under floor convector and 2 x 1 kW) -OPTION 3: Include an smoke detector in the return airflow area inside the HVAC unit -OPTION 4: WC PMR heater 500W -OPTION 5: WC PMR Temperature sensor -OPTION 6: WC Damper for pressure wave protection -OPTION 7: Pressure wave protection device -OPTION 8: Heat pump in one of the HVAC circuits -OPTION 9: Third stage of heating resistors inside the HVAC unit (instead of the two stage commonly used). | EFB-RS-899 | The Scope of Supply of the System will include at least following components per car, that will be described in more detail in each section of this specification: - Two EC compacts HVAC units per car including each of them: - 1 reversable cooling circuit. Approximated cooling power 28 kW at 40ºC 43%RH, to be justified by thermal calculations. Heating power 20 kW at -10ºC outside and 22ºC inside. - air filters - temperature sensors, thermostats, pressure gauges, pressure switches... - double sealing barrier in the interface with the carbody structure to avoid any water getting into the saloon area. - electrical connectors - 1 electric control panel including the protections and control components for the HVAC unit, including the electronic controller equipped with Ethernet port. - Exhaust system inside the HVAC unit - temperature sensors to be installed outside the HVAC unit, in case they are required -OPTION 1: CO2 detector to regulate the fresh airflow -OPTION 2: Floor Heat convectors. Approximated total floor heating power 15 kW: (6 x 1,8 kW under floor convector and 3 x 1,5 kW) -OPTION 3: Include an smoke detector in the return airflow area inside the HVAC unit -OPTION 4: WC PMR heater 500W -OPTION 5: WC PMR Temperature sensor -OPTION 6: WC Damper for pressure wave protection -OPTION 7: Pressure wave protection device -OPTION 8: Heat pump based on a single circuit solution | 67.2453 | C | HC_230517: scope of supply oncluide on base solution: - Two EC compact HVAC unit per car including each of them: - 1 reversable cooling circuit. Cooling power 27,6 kW at 40ºC 43%RH. - Heating power 20 kW at -10ºC outside and 22ºC inside. - Cartridge air filters - temperature sensors, thermostats, pressure gauges, pressure switches... - double sealing barrier in the interface with the carbody structure to avoid any water getting into the saloon area. - electrical connectors - 1 electric control panel including the protections and control components for the HVAC unit, including the electronic controller equipped with Ethernet port - Evaporator DC Blower. - Condenser AC blower - Exhaust system inside the HVAC unit OPTION 1: CO2 sensor Offered as optional. OPTION 2: Heat convectors Offered as optional. OPTION 3: Smoke Detector Offered as optional. OPTION 4: WC/PMR heater 500 W Offered as optional OPTION 5: WC/PMR temperature sensor Offered as optional. OPTION 6: agreed not Offered. OPTION 7: agreed not Offered. OPTION 8: Offered as optional. | C | HC_230517: scope of supply oncluide on base solution: - Two EC compact HVAC unit per car including each of them: - 1 reversable cooling circuit. Cooling power 27,6 kW at 40ºC 43%RH. - Heating power 20 kW at -10ºC outside and 22ºC inside. - Cartridge air filters - temperature sensors, thermostats, pressure gauges, pressure switches... - double sealing barrier in the interface with the carbody structure to avoid any water getting into the saloon area. - electrical connectors - 1 electric control panel including the protections and control components for the HVAC unit, including the electronic controller equipped with Ethernet port - Evaporator DC Blower. - Condenser AC blower - Exhaust system inside the HVAC unit OPTION 1: CO2 sensor Offered as optional. OPTION 2: Heat convectors Offered as optional. OPTION 3: Smoke Detector Offered as optional. OPTION 4: WC/PMR heater 500 W Offered as optional OPTION 5: WC/PMR temperature sensor Offered as optional. OPTION 6: agreed not Offered. OPTION 7: agreed not Offered. OPTION 8: Offered as optional.
EFB-RS-248 | Two temperature sensors of each type shall be installed on the HVAC unit in order to achieve the redundancy level required (supply air, return air, fresh air) | EFB-RS-905 | Two temperature sensors of each type shall be installed on each HVAC unit in order to achieve the redundancy level required (supply air, return air, fresh air) | 66 | NC | HC_230517:En el caso de que falle un sensor en el equipo 1, el equipo 2 pueda enviar los valores al equipo 1, podríamos ir con un sensor para cada equipo en lugar de dos para cada equipo. Seria necesario que el TCMS devolviera los valores medidos por los equipos al bus de comunicaciones. | NC | HC_230517:En el caso de que falle un sensor en el equipo 1, el equipo 2 pueda enviar los valores al equipo 1, podríamos ir con un sensor para cada equipo en lugar de dos para cada equipo. Seria necesario que el TCMS devolviera los valores medidos por los equipos al bus de comunicaciones.
EFB-RS-378 | In case of failure of an element in the condenser section (i.e condenser fan), the HVAC unit shall still in operation ensuring 50% of the cooling/heating perforance of the unit. | EFB-RS-909 | In case of failure of an element in the condenser section (i.e condenser fan) in one of the units, the other HVAC unit shall still in operation ensuring 50% of the cooling/heating saloon performance required. | 66 | C |  | C
EFB-RS-390 | The Supplier shall confirm during the tender stage if the proposed heating power distribution (35-40 kW overhead and around 14 kW floor heating solution) is adequate in order to provide a correct temperature uniformity even at minimum temperature. | EFB-RS-910 | The Supplier shall confirm during the tender stage if the proposed heating power distribution (40 kW overhead and around 15 kW floor heating solution per unit) is adequate in order to provide a correct temperature uniformity even at minimum temperature. | 66 | C |  | C
EFB-RS-224 | The HVAC system shall be able to start 1 or 2 cooling circuits after 2 hours under maximum solar radiation, and considering 50ºC ambient temperature. | EFB-RS-904 | The HVAC system shall be able to start cooling circuit after 2 hours under maximum solar radiation, and considering 50ºC ambient temperature. | 59.4 | C |  | C
EFB-RS-711 | The HVAC and the interface to the carbody shall be able to withstand a pressure difference of +/- 2500 Pa without loosing the pressure tightness | EFB-RS-871 | The HVAC and the interface to the carbody shall be able to withstand a pressure difference of +/- 2500 Pa | 59.4 | NA | HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER | NA | V0: METRO ESSEN HC_230517: Acording to CAF instructions, pressure wave proteccions only apply to MD, not to P2 CER
EFB-RS-533 | Air renewal may vary depending on the operating mode of the equipment, and interior and exterior air quality and conditions. The number of persons to be considered for the dimensioning of the flow rates is all seated places. The flow rate is regulated by the following modes: | EFB-RS-932 | Air renewal may vary depending on the operating mode of the equipment, and interior and exterior air quality and conditions. The number of people to be accounted for when calculating passenger flows comprises all seated places and 2 people per metre squared in standing areas (car to car). The flow rate is regulated by the following modes: | 59.4 | C |  | C
EFB-RS-392 | The overhead heating power shall be divided in 2 stages. The Supplier shall propose during the tender stage the power per stage. As OPTION 9 a third stage of overhead heating shall be proposed in order to achieve the preheating condition. The power distribution between the different stages shall be discussed with in project phase. As a preliminary stimation, CAF propose to consider a 20 kW heating power for the third stage. | EFB-RS-921 | The overhead heating power shall be divided in 2 stages. The Supplier shall propose during the tender stage the power per stage. The power distribution between the different stages shall be discussed with in project phase. | 52.8 | C |  | C
EFB-RS-194 | Each train consist on the following compositions: - TEB: 3 car unit: A1-B1-A2 - TEA: 5 car unit: A1-B1-B2-B3-A2 | EFB-RS-897 | Each train consist on the following compositions: - TEB: 4 car unit: A1-B1-B2-A2 - TEA: 5 car unit: A1-B1-B2-B3-A2 | 49.5 | C |  | NC
EFB-RS-277 | There shall be 2 control panels per unit to achieve the level of redundancy required. Control panels shall be located inside the HVAC unit and accesible from inside the car. | EFB-RS-917 | There shall be one control panel per unit to achieve the level of redundancy required. Control panels shall be located inside the HVAC units and accesible from inside the car. | 49.5 | C |  | C
EFB-RS-359 | In case of failure of an element in the evaporator section (i.e evaporator fan), the HVAC unit shall still in operation ensuring 50% of the cooling/heating perforance of the unit. | EFB-RS-907 | In case of failure of an element in the evaporator section (i.e evaporator fan) in one of the units, the other HVAC unit shall still in operation, ensuring 50% of the cooling/heating saloon performance required. | 49.5 | C |  | C
EFB-RS-460 | In the event of failure in both cooling circuits of the HVAC unit the HVAC unit will follow working in ventilation mode. The HVAC unit shall provide ventilation with normal fresh air intake and return air circulation. | EFB-RS-901 | In the event of failure in the cooling circuit of the HVAC units, the HVAC unit will follow working in ventilation mode. The HVAC units shall provide ventilation with normal fresh air intake and return air circulation. | 49.5 | C |  | C
EFB-RS-826 | A heat pump function shall be considered as OPTION 8 in one of the cooling circuits of the HVAC system. | EFB-RS-913 | A heat pump function shall be considered as OPTION 8 in the HVAC system. | 49.5 | C |  | C
EFB-RS-835 | Return air opening dimensions. | EFB-RS-474 | Additionally the Supplier will be responsible of including following tests in the test specification and doing these type test in factory CAF together with the CAF personnel, in order to demonstrate the correct design of the drainage of the HVAC system once mounted in the train. A proposal for these test will be as follows. Part 1. Test with the HVAC system completely stopped: 1.a) Throw a water flow of 1.5 times X(l/min) in the evaporator drain pan. Check that all the draining ports open, and no water is stagnant in the pan. Check that there is not any water leak in the joinings between the HVAC system and the train draining pipework. 1.b) Throw a water flow of 1.5 times Z(l/min) in the condenser drain pan. Check that all the draining ports open, and no water is stagnant in the pan. Check that there is not any water leak in the joinings between the HVAC system and the train draining pipework. 1.c) Throw a water flow of 1.5 times Y(l/min) in the fresh air inlet. Check that all the draining ports open, and no water is stagnant in the pan. Check that there is not any water leak in the joinings between the HVAC system and the train draining pipework. Part 2: Test with the HVAC system in maximum cooling mode 2.a) Throw a water flow of 1.5 times X(l/min) in the evaporator drain pan. Check that all the water is drained correctly and no water is dripping in the supply air ducting or the passenger area. 2.b) Throw a water flow of 1.5 times Z(l/min) in the condenser drain pan. Check that all the water is drained correctly and no water is dripping in the passenger area. 2.c) Throw a water flow of 1.5 times Y(l/min) in the fresh air inlet. Check that all the water is drained correctly and no water is dripping in the supply air ducting or the passenger area. | 49.5 | NA | HC_230517:These tess are included in Z4 position factory test by CAF, and performed by CAF, just in case of problems detected during the testing HC will be inform and call to give support. NA, because it's done in Z4. This test is also done in the origin type test, but this is not what is described in this requirement. this requirement refers to the factory type test, and generally this test is carried out in the earliest project phase possible, normally at same time than Z4 test (carried out by CAF). Later, during the Factory Type test, the drainage system is checked again during the cooling test. In any case, HC will always support CAF if necessary. | NA | HC_230517:These tess are included in Z4 position factory test by CAF, and performed by CAF, just in case of problems detected during the testing HC will be inform and call to give support. NA, because it's done in Z4. This test is also done in the origin type test, but this is not what is described in this requirement. this requirement refers to the factory type test, and generally this test is carried out in the earliest project phase possible, normally at same time than Z4 test (carried out by CAF). Later, during the Factory Type test, the drainage system is checked again during the cooling test. In any case, HC will always support CAF if necessary.
EFB-RS-834 | The dimensions of the return air opening of the saloon HVAC shall not exceed 600 mm in width to avoid interference with the supply ducts and 450 mm in length to ensure that the return air opening is located in the vestibule area and does not interfere with the door mechanism. | EFB-RS-916 | The dimensions of the return air opening of the saloon HVAC shall not exceed 600 mm in width to avoid interference with the supply ducts. | 39.6 | C |  | C
EFB-RS-712 | The floor heating convectors distribution to be considered shall be as follows: - A1 and A2 cars: - 6 underseat floor convectors (1,5 kW) - 2 platform converctors (1 kw) - B1 car: - 6 underseat floor convectors (1,5 kW) | EFB-RS-911 | The preliminary floor heating convectors distribution to be considered shall be as follows: - A1 and A2 cars: - 7 underseat floor convectors (1,8 kW) - 2 tip up converctors (1,5 kw) - B1 and B2 car: - 7 underseat floor convectors (1,8 kW) - 1 underseat floor convectors (1,5 kW) | 37.125 | C |  | C
EFB-RS-447 | The saloon HVAC Unit of the single car shall not exceed the following length 3150 mm | EFB-RS-915 | The saloon HVAC Units of the single car shall not exceed the following length 2050 mm | 33 | NC | HC_230517: 2200 mm | NC | HC_230517: 2200 mm
EFB-RS-461 | In the event of a single failure in one of the components of the HVAC units (compressor, evaportor fan, condenser fan, electronic) the unit shall still providing 50 % of the performance capacity. | EFB-RS-902 | In the event of a single failure in one of the HVAC units (compressor, evaporator fan, condenser fan, electronic) the other unit shall remaing working to provide the 50 % of the total capacity needed per car. | 28.2857 | C |  | C
EFB-RS-170 | The forced extraction shall be able to wihtstand a pressure loss of the ducts above 100 Pa @ 900 m3/h. | EFB-RS-839 | The forced extraction shall be able to withstand a pressure loss of the ducts above 200 Pa @ 1315 m3/h (per HVAC). | 24.75 | C |  | C
EFB-RS-528 | - train occupancy for the calculation of the heating capacity is considered to be zero. | EFB-RS-512 | - The speed of the car is considered to be zero. | 24.75 | C |  | C
EFB-RS-709 | Extraction supplier shall provide proof the installed equipment is sealed and pressure tight | EFB-RS-147 | A saloon HVAC noise test report shall be supplied to CAF for approval which shall include, as a minimum: · Reference to the standard according to which the measurements have been performed · A description of the test set up: - Image of the equipment installation - Description of the instalation environment - Description of fixation points (and description of elastic mountings if necessary) · A description of the measurement points (for SPL) and surfaces (for SWL) · Sound pressure measurements: - Description of the operating conditions for each case and equipment component (evaporator rpm, airflow, number of compressors working, etc.) - The sound pressure measurement results with A frequency weighting - 1/3 octave band analysis of each measurement point for each operating condition (tabulated) for each point - Pass/fail analysis · Sound power measurements: - Description of how sound power is obtained - Description of the operating conditions for each case and equipment component (evaporator rpm, airflow, number of compressors working, etc.) - The sound power measurement results with A frequency weighting - 1/3 octave band analysis of the Sound Power Level for each operating condition (tabulated) for each surface and overall - Pass/fail analysis · Pure tone analysis: - Pass/fail analysis according the Annex K of the method described in ISO 1996-2:2017. Note: Background noise shall be measured. In case the background noise is not 10 dB lower than the noise measured, the corrections shall be done according to the Table 1 of the standard ISO 3095:2005, and shall be documented in the test report. | 24.75 | C |  | C
EFB-RS-562 | § Each unit offers redundancy in the event of a single failure of one of the components associated with one of the cooling circuits (compressors, evaporator fans, condenser fans). In addition, each of these elements has its corresponding protection. Therefore, as the equipment has a double refrigeration circuit, in the event of failure of any of these elements, the train can continue to maintain 50% of its performance. The HVAC equipment will transmit the corresponding alarm to the TCMS to be signalled accordingly. | EFB-RS-925 | Each car provides redundancy in the event of a single failure. Each car is equipped with two HVAC units, whereby should one component associated to one of the HVAC units fail, 50% of the performance is maintained with the remaining HVAC unit. The HVAC equipment will transmit the corresponding alarm to the TCMS to be signalled accordingly. | 22 | C |  | C
EFB-RS-502 | For this purpose, the redundancy of each saloon HVAC equipment is supported by both two identical thermodynamic circuits and two identical control electronic systems, so as to ensure that in case of failure of any element, at least 50% of the HVAC is available in each car. | EFB-RS-501 | The HVAC system is redundant in each passenger car and in all aspects (thermodynamic and electronic). In the event of a breakdown of any element (of any kind), at least 50% of the HVAC is available in each car. | 19.8 | C |  | C
EFB-RS-524 | - train occupancy for the calculation of the cooling capacity is 100% of passengers per car (considering the total capacity offered in seated places). | EFB-RS-520 | The following conditions have been considered for the calculation of the cooling and heating demand: | 16.5 | C |  | C
EFB-RS-200 | One compact type HVAC unit, with EC aquitecture (Evaporator - Condenser section) with all equipment required for satisfactory functioning of the system, shall be provided for each car. | EFB-RS-931 | The required power demand has been calculated from the calculations under the above conditions. The installed capacity has been increased by 15% compared to all previous conditions (pre-cooling, pre-heating, heating and cooling). The worst case car was taken into account. A2. As the units installed on the cars are identical, the other cars will benefit from a greater increase in installed power compared to this least advantageous car. | 14.1429 | C |  | C
EFB-RS-163 | The preconditioning time shall be calculated according the following volume for the following cars: Volume car B1: 140,6 m3 Volume car A2: 159,35 m3 Volumen car A2 (without considering electric cabinets area): 135,53 m3 | EFB-RS-838 | The preconditioning time shall be calculated according to A2 car volume: 157,75 m3 | 12.375 | C |  | C
EFB-RS-728 | - En caso de que se haya dejado encendido el sistema de climatización de sala antes de pasar al modo Ahorro de Energía, éste pasará a trabajar en un rango de temperatura inferior, entre 10ºC y 30ºC. En caso de que estuviera apagado antes de entrar al modo Ahorro de energía, el sistema de climatización permanecerá apagado. | EFB-RS-509 | Following the philosophy of the European Union, Regulation (EU) No. 517/2014 of the European Parliament and of the Council of 16 April 2014 on fluorinated greenhouse gases, measures will be adopted to reduce emissions of hydrofluorocarbons (HFCs), and to achieve more climate-friendly technologies in new equipment and products. Coolant R513A with a lower impact than other refrigerant fluids currently used in the railway sector will be used. | 8.25 | C |  | C
EFB-RS-152 | En lo relativo a revestimientos y elementos de interiorismo a continuación, se describen algunas de las medidas tomadas en la sujeción de los mismos para evitar la existencia de ruidos y vibraciones molestas para los viajeros o el personal a bordo. | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS | 0 | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS
EFB-RS-153 | - Equipos de climatización montados en techo: los compresores y los ventiladores de evaporadora/condensadora pueden producir vibraciones que se transmitan hacia el interior. Se montan elementos elásticos para aislar las vibraciones producidas por los compresores de la zona de condensadora del HVAC. | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS | 0 | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS
EFB-RS-373 | Each Saloon HVAC system will be fitted with 2 compressors, one per cooling circuit. | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS | 0 | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS
EFB-RS-440 | Each Saloon HVAC system will consist of a single frame divided in 2 separated areas: -evaporator 1 -condenser Each area shall be defined in such a way to guarantee 50% of cooling and heating performance in case of failure of 1 evaporator or condenser fan. | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS | 0 | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS
EFB-RS-462 | The HVAC system will provide 2 cooling circuits, and all the elements in the circuit will be controlled independently of the elements in the other circuit. Fully redundant cooling circuit, control and protection devices will be provided. There shall be suitable circuit breakers and contactors to protect separately each evaporator motor, each condenser motor, each compressor and each heating stage. | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS | 0 | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS
EFB-RS-486 | The Train is equipped with independent HVAC equipment centred on the roof of each car. | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS | 0 | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS
EFB-RS-561 | § In case of failure of the electronics: the equipment has redundant electronics, so that, in case of failure of one of the electronics, the equipment can continue providing 50% of performance with the remaining electronics. | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS | 0 | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS
EFB-RS-705 | HVAC supplier shall provide proof the installed equipment is sealed and pressure tight | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS | 0 | NO HAY COINCIDENCIAS | NO HAY COINCIDENCIAS